## Start here
869-MTR — Multilin 869 motor protection
How to use this workbook
Fill in | Only the two shaded columns on each test sheet: MEASURED and PASS / FAIL. Everything else is calculated and should not be edited by hand.
Example row | MEASURED "1.432 s", PASS / FAIL "PASS". Use the same unit the Expected column uses, so the two can be compared without conversion.
Untested steps | Record them as NOT TESTED with a reason. A blank result reads as work not yet done; it must never be left blank on a completed record.
If a setting changes | Do not edit numbers here. Change it in the relay tool, re-run the generator, and rebuild this workbook — that is what keeps the injected values and the calculations from drifting apart.
Where these values come from
Plan | 869-MTR — Multilin 869 motor protection
Generated | generated 2026-09-05 12:27 from 869.html
Configuration | kv=4.16; fla=180; sf=1.15; hp=1500; pf=0.89; freq=60; rot=ABC; type=ind; lra=6; lrtc=20; lrth=15; acc=8; start=3; tbs=20; cmode=std; cm=4; ca=87.4; cn=2; cref=fla; fitI=6; fitT=10; k=6; hcr=0.75; taur=15; taus=30; tau_i=20; kf=1.05; ctp=200; cts=5; ctgp=50; ctgs=5; vtp=4160; vts=120; vtc=wye; diff=cb; cmc=3x; imax=32; vmax=300
Conventions | All quantities are SECONDARY at the relay terminals. Angles in degrees, CCW positive, V L1 = 0.
Sample data | Values shown are for the tool's sample configuration — re-generate after entering real station data.
Record identification
Station
Feeder / plant item
Device serial
Firmware
Setting file revision
Test set serial
Tested by
Date
Witnessed by
Sheets in this workbook
Test steps | 92 test steps — the record. Fill in MEASURED and PASS / FAIL.
Channels | 548 rows — one per channel per step, for pasting into a Test Universe module table.
Build guide | How to assemble this plan in Test Universe, and the thing about this relay most likely to be got wrong.
Progress
Total steps
Results entered
Passed
Failed
Not tested
Outstanding
Counts refer to the first test sheet only.

## Test steps
Function | Description | TU module | Drive as | # | Test step | What is applied | Run | State | Dur s | V L1 | V L2 | V L3 | I L1 | I L2 | I L3 | Hz | Reachable | Expected | Expected — detail | MEASURED | PASS / FAIL
49 | Thermal overload model | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of the 1.15 ×FLA overload pickup |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 5.4337@-27.1 | 5.4337@-147.1 | 5.4337@92.9 | 60 | yes | OPERATE | Very long — 12.72 min from the curve
49 | Thermal overload model | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of the 1.15 ×FLA overload pickup |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.9162@-27.1 | 4.9162@-147.1 | 4.9162@92.9 | 60 | yes | RESTRAIN | No accumulation
49 | Thermal overload model | Overcurrent | characteristic | 3 | Timing at 1.50 ×FLA | balanced · cold curve |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 6.7500@-27.1 | 6.7500@-147.1 | 6.7500@92.9 | 60 | yes | 4.66 min | From the cold overload curve
49 | Thermal overload model | Overcurrent | characteristic | 4 | Timing at 2.00 ×FLA | balanced · cold curve |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 9.0000@-27.1 | 9.0000@-147.1 | 9.0000@92.9 | 60 | yes | 116.5 s | From the cold overload curve
49 | Thermal overload model | Overcurrent | characteristic | 5 | Timing at 3.00 ×FLA | balanced · cold curve |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 13.5000@-27.1 | 13.5000@-147.1 | 13.5000@92.9 | 60 | yes | 43.7 s | From the cold overload curve
49 | Thermal overload model | Overcurrent | characteristic | 6 | Timing at 4.00 ×FLA | balanced · cold curve |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 18.0000@-27.1 | 18.0000@-147.1 | 18.0000@92.9 | 60 | yes | 23.3 s | From the cold overload curve
49 | Thermal overload model | Overcurrent | characteristic | 7 | Timing at 6.00 ×FLA | balanced · cold curve |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | 9.99 s | From the cold overload curve
49TC | Thermal capacity and lockout | Quick CMC | points | 1 | Accumulate at 2.0 ×FLA | Capacity rises at 0.858 % per second from a cold start |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 9.0000@-27.1 | 9.0000@-147.1 | 9.0000@92.9 | 60 | yes | 87.4 s to alarm | Trip at 116.5 s · hold the current, do not interrupt it
49TC | Thermal capacity and lockout | Quick CMC | points | 2 | Accumulate at 4.0 ×FLA | Capacity rises at 4.291 % per second from a cold start |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 18.0000@-27.1 | 18.0000@-147.1 | 18.0000@92.9 | 60 | yes | 17.5 s to alarm | Trip at 23.3 s · hold the current, do not interrupt it
49TC | Thermal capacity and lockout | Quick CMC | points | 3 | Accumulate at 6.0 ×FLA | Capacity rises at 10.011 % per second from a cold start |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | 7.49 s to alarm | Trip at 9.99 s · hold the current, do not interrupt it
49TC | Thermal capacity and lockout | Quick CMC | points | 4 | Decay — 5 min stopped | From 100% used, current removed, motor stopped. τ stopped is 30 min. |  |  |  | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 84.6% remaining | Restart permitted below 100%
49TC | Thermal capacity and lockout | Quick CMC | points | 5 | Decay — 15 min stopped | From 100% used, current removed, motor stopped. τ stopped is 30 min. |  |  |  | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 60.7% remaining | Restart permitted below 100%
49TC | Thermal capacity and lockout | Quick CMC | points | 6 | Decay — 30 min stopped | From 100% used, current removed, motor stopped. τ stopped is 30 min. |  |  |  | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 36.8% remaining | Restart permitted below 100%
49TC | Thermal capacity and lockout | Quick CMC | points | 7 | Decay — 60 min stopped | From 100% used, current removed, motor stopped. τ stopped is 30 min. |  |  |  | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 13.5% remaining | Restart permitted below 100%
48 | Acceleration time / incomplete sequence | State Sequencer | sequence | 1 | Stopped | No current, motor at rest | 1 | 1/3 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | READY | Start supervision idle
48 | Acceleration time / incomplete sequence | State Sequencer | sequence | 2 | Successful start — acceleration | Current stepped to 6.00 ×FLA and held for the nameplate acceleration time of 8.00 s | 1 | 2/3 | 8 | 58.890@0.0 | 58.890@-120.0 | 58.890@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | NO TRIP | Inside the 10.0 s limit
48 | Acceleration time / incomplete sequence | State Sequencer | sequence | 3 | Successful start — running | Current dropped to full load, below the 1.40 ×FLA transition level | 1 | 3/3 | 10 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | START COMPLETE | Acceleration timer resets
48 | Acceleration time / incomplete sequence | State Sequencer | sequence | 4 | Stalled start — stopped | No current, motor at rest | 2 | 1/2 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | READY
48 | Acceleration time / incomplete sequence | State Sequencer | sequence | 5 | Stalled start — current never drops | Current held at 6.00 ×FLA past the 10.0 s limit — the motor never accelerates | 2 | 2/2 | 13 | 58.890@0.0 | 58.890@-120.0 | 58.890@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | TRIP AT 10.0 s | Incomplete sequence, or the thermal curve first — see the note below
51LR | Locked rotor and mechanical jam | Overcurrent | pickup+time | 1 | Jam — above pickup | 105% of the jam setting, motor already running |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 11.8125@-27.1 | 11.8125@-147.1 | 11.8125@92.9 | 60 | yes | TRIP | Operate after 1.00 s
51LR | Locked rotor and mechanical jam | Overcurrent | pickup+time | 2 | Jam — below pickup | 95% of the jam setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 10.6875@-27.1 | 10.6875@-147.1 | 10.6875@92.9 | 60 | yes | NO TRIP | No operation
51LR | Locked rotor and mechanical jam | Overcurrent | pickup+time | 3 | Locked rotor — above pickup | 105% of the locked-rotor setting, applied from standstill |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 21.2625@-27.1 | 21.2625@-147.1 | 21.2625@92.9 | 60 | yes | TRIP | Operate after 2.00 s
51LR | Locked rotor and mechanical jam | Overcurrent | pickup+time | 4 | Jam blocked during start | Full locked-rotor current applied from standstill — the jam element must stay blocked for the first 10.0 s |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | JAM BLOCKED | A normal start must not look like a jam
66 | Starts per hour / time between starts | State Sequencer | sequence | 1 | Start 1 of 3 | Locked-rotor current for 8.00 s, then run | 1 | 1/10 | 8 | 58.890@0.0 | 58.890@-120.0 | 58.890@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | PERMITTED | Counter advances to 1
66 | Starts per hour / time between starts | State Sequencer | sequence | 2 | Run after start 1 | Full load, counter holding at 1 | 1 | 2/10 | 30 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | RUNNING | 2 starts left in the hour
66 | Starts per hour / time between starts | State Sequencer | sequence | 3 | Stopped after start 1 | Current removed | 1 | 3/10 | 5 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | STOPPED | Restart delay of 60.0 s begins
66 | Starts per hour / time between starts | State Sequencer | sequence | 4 | Start 2 of 3 | Locked-rotor current for 8.00 s, then run | 1 | 4/10 | 8 | 58.890@0.0 | 58.890@-120.0 | 58.890@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | PERMITTED | Counter advances to 2
66 | Starts per hour / time between starts | State Sequencer | sequence | 5 | Run after start 2 | Full load, counter holding at 2 | 1 | 5/10 | 30 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | RUNNING | 1 start left in the hour
66 | Starts per hour / time between starts | State Sequencer | sequence | 6 | Stopped after start 2 | Current removed | 1 | 6/10 | 5 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | STOPPED | Restart delay of 60.0 s begins
66 | Starts per hour / time between starts | State Sequencer | sequence | 7 | Start 3 of 3 | Locked-rotor current for 8.00 s, then run | 1 | 7/10 | 8 | 58.890@0.0 | 58.890@-120.0 | 58.890@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | PERMITTED | Counter advances to 3
66 | Starts per hour / time between starts | State Sequencer | sequence | 8 | Run after start 3 | Full load, counter holding at 3 | 1 | 8/10 | 30 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | RUNNING | No starts left
66 | Starts per hour / time between starts | State Sequencer | sequence | 9 | Stopped after start 3 | Current removed | 1 | 9/10 | 5 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | STOPPED | Restart delay of 60.0 s begins
66 | Starts per hour / time between starts | State Sequencer | sequence | 10 | Start 4 — refused | Attempt one more start inside the same hour | 1 | 10/10 | 60 | 58.890@0.0 | 58.890@-120.0 | 58.890@120.0 | 27.0000@-27.1 | 27.0000@-147.1 | 27.0000@92.9 | 60 | yes | START INHIBITED | The relay must block the close, not trip after it
46 | Current unbalance | Overcurrent | characteristic | 1 | Ratio — above threshold | I2/I1 = 16.5% · L3 reduced to 57.5% · Ieq 0.926 ×FLA |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 2.5880@92.9 | 60 | yes | OPERATE | Operate after 5.00 s
46 | Current unbalance | Overcurrent | characteristic | 2 | Ratio — below threshold | I2/I1 = 13.5% · L3 reduced to 64.3% · Ieq 0.928 ×FLA |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 2.8943@92.9 | 60 | yes | RESTRAIN | No operation
46 | Current unbalance | Overcurrent | characteristic | 3 | Alarm threshold | I2/I1 = 10.0% · below the trip ratio |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 3.2727@92.9 | 60 | yes | ALARM ONLY | Alarm asserts, trip does not
46 | Current unbalance | Overcurrent | characteristic | 4 | Single phasing | L3 taken to zero — the deepest a single open phase can go |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 0.0000@92.9 | 60 | yes | OPERATE | I2/I1 = 50%, the ceiling for this method
46 | Current unbalance | Overcurrent | characteristic | 5 | Reverse rotation | Balanced set with L2 and L3 exchanged — all negative sequence |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@92.9 | 4.5000@-147.1 | 60 | yes | OPERATE | I2/I1 is undefined with I1 at zero; the element should see full unbalance
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 1 | Pickup — below threshold | 95% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 2.5650@-27.1 | 2.5650@-147.1 | 2.5650@92.9 | 60 | yes | TRIP | Operate after 5.00 s
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 2 | Pickup — above threshold | 105% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 2.8350@-27.1 | 2.8350@-147.1 | 2.8350@92.9 | 60 | yes | NO TRIP | No operation
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 3 | Timing at half pickup | Step from full load straight down |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 1.3500@-27.1 | 1.3500@-147.1 | 1.3500@92.9 | 60 | yes | 5.00 s | Definite time
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 4 | Motor stopped | No current at all — an open contactor must not read as loss of load |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0000@-27.1 | 0.0000@-147.1 | 0.0000@92.9 | 60 | yes | NO TRIP | Element supervised by the run status
87M | Motor differential | Quick CMC | points | 1 | Sensitivity — above pickup | One conductor through the window carrying 0.220 A primary equivalent |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0220@0.0 |  |  | 60 | yes | OPERATE | Operate within 0.03 s
87M | Motor differential | Quick CMC | points | 2 | Sensitivity — below pickup | One conductor through the window carrying 0.180 A primary equivalent |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0180@0.0 |  |  | 60 | yes | RESTRAIN | No operation
87M | Motor differential | Quick CMC | points | 3 | Through-current stability | All three phase leads bundled through the window in the correct direction at 4.0 ×FLA |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 18.0000@0.0 | 18.0000@-120.0 | 18.0000@120.0 | 60 | yes | RESTRAIN | A balanced set through the window sums to zero
50P | Short circuit | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · 37.800 A secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 37.8000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50P | Short circuit | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · 34.200 A secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 34.2000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50P | Short circuit | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 72.0000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.05 s | Measured from application of current to trip
50G | Ground instantaneous | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · 0.525 A secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.5250@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50G | Ground instantaneous | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · 0.475 A secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.4750@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50G | Ground instantaneous | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 1.0000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.05 s | Measured from application of current to trip
51G | Ground time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.3150@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51G | Ground time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.2850@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51G | Ground time OC | Overcurrent | characteristic | 3 | Timing at 2.0× pickup | IEC Curve A (SI) · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.6000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 2.01 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 4 | Timing at 3.0× pickup | IEC Curve A (SI) · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.9000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.26 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 5 | Timing at 5.0× pickup | IEC Curve A (SI) · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 1.5000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.86 s | Predicted from the curve equation
50SG | Sensitive ground | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · 0.053 A secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0525@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50SG | Sensitive ground | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · 0.048 A secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0475@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50SG | Sensitive ground | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.1000@-30.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.05 s | Measured from application of current to trip
50BF | Breaker or contactor failure | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold | 105% of the detector setting, no initiate |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.9450@-27.1 | 0.9450@-147.1 | 0.9450@92.9 | 60 | yes | DETECTOR PICKED UP | Flag only, no trip without initiate
50BF | Breaker or contactor failure | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold | 95% of the detector setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.8550@-27.1 | 0.8550@-147.1 | 0.8550@92.9 | 60 | yes | NO PICKUP | Detector must drop out
50BF | Breaker or contactor failure | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | Initiate asserted with current held and never removed |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 2.7000@-27.1 | 2.7000@-147.1 | 2.7000@92.9 | 60 | yes | 0.10 s | Timer 1
50BF | Breaker or contactor failure | State Sequencer | sequence (assemble from these steps) | 4 | Upstream trip timing | Same state, second stage |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 2.7000@-27.1 | 2.7000@-147.1 | 2.7000@92.9 | 60 | yes | 0.25 s | Timer 2 — trips the feeding breaker
50BF | Breaker or contactor failure | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | Initiate asserted, then current removed inside timer 1 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0000@-27.1 | 0.0000@-147.1 | 0.0000@92.9 | 60 | yes | NO TRIP | Proves the detector reset stops the scheme
27 | Undervoltage | Voltage | pickup+time | 1 | Pickup — below threshold | 95% of setting, motor on load |  |  |  | 52.654@0.0 | 52.654@-120.0 | 52.654@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | OPERATE | Operate after 3.00 s
27 | Undervoltage | Voltage | pickup+time | 2 | Pickup — above threshold | 105% of setting |  |  |  | 58.197@0.0 | 58.197@-120.0 | 58.197@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | RESTRAIN | No operation
27 | Undervoltage | Voltage | pickup+time | 3 | Timing at 0.50× pickup | Step from nominal to the test level |  |  |  | 27.713@0.0 | 27.713@-120.0 | 27.713@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | 3.00 s | Definite time
27 | Undervoltage | Voltage | pickup+time | 4 | Below minimum operating voltage | Proves the element blocks rather than operating on a dead starter |  |  |  | 4.000@0.0 | 4.000@-120.0 | 4.000@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | BLOCKED | Element inhibited
27 | Undervoltage | Voltage | pickup+time | 5 | During a start | Voltage dips on every start. The element must be inhibited for 5.00 s or ride it through. |  |  |  | 55.426@0.0 | 55.426@-120.0 | 55.426@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | NO TRIP | A healthy start must not trip on undervoltage
59 | Overvoltage | Voltage | pickup+time | 1 | Pickup — above threshold | 105% of setting, motor on load |  |  |  | 80.021@0.0 | 80.021@-120.0 | 80.021@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | OPERATE | Operate after 2.00 s
59 | Overvoltage | Voltage | pickup+time | 2 | Pickup — below threshold | 95% of setting |  |  |  | 72.400@0.0 | 72.400@-120.0 | 72.400@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | RESTRAIN | No operation
59 | Overvoltage | Voltage | pickup+time | 3 | Timing at 1.25× pickup | Step from nominal to the test level |  |  |  | 95.263@0.0 | 95.263@-120.0 | 95.263@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | 2.00 s | Definite time
47 | Voltage unbalance / phase reversal | Quick CMC | points | 1 | Pickup — above threshold | Balanced set in reverse rotation — every volt applied is negative sequence |  |  |  | 6.097@0.0 | 6.097@120.0 | 6.097@-120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 2.00 s
47 | Voltage unbalance / phase reversal | Quick CMC | points | 2 | Pickup — below threshold | Balanced set in reverse rotation — every volt applied is negative sequence |  |  |  | 4.988@0.0 | 4.988@120.0 | 4.988@-120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
47 | Voltage unbalance / phase reversal | Quick CMC | points | 3 | Full phase reversal | Nominal balanced set with L2 and L3 exchanged — the motor would run backwards |  |  |  | 69.282@0.0 | 69.282@120.0 | 69.282@-120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Must block the start, not trip after it
81 | Under / over frequency | Quick CMC | points | 1 | Pickup — past threshold | 0.100 Hz beyond the setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 56.9 | yes | OPERATE | Operate after 2.00 s
81 | Under / over frequency | Quick CMC | points | 2 | Pickup — short of threshold | 0.100 Hz on the healthy side |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 57.1 | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 3 | Timing | Step from 60.0 Hz straight to 56.900 Hz |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 56.9 | yes | 2.00 s | Definite time
81 | Under / over frequency | Quick CMC | points | 4 | Below minimum voltage | Frequency past the setting but voltage under the 30 V supervision level |  |  |  | 24.000@0.0 | 24.000@-120.0 | 24.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 56.9 | yes | BLOCKED | Element inhibited
55 | Power factor | Quick CMC | points | 1 | Past the limit | 5° beyond the setting angle |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@50.6 | 4.5000@-69.4 | 4.5000@170.6 | 60 | yes | OPERATE | pf = 0.635 leading
55 | Power factor | Quick CMC | points | 2 | Short of the limit | 5° inside the setting angle |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@40.6 | 4.5000@-79.4 | 4.5000@160.6 | 60 | yes | RESTRAIN | pf = 0.760 leading
55 | Power factor | Quick CMC | points | 3 | Full VAR, no watts | Current in quadrature — power factor zero |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@90.0 | 4.5000@-30.0 | 4.5000@-150.0 | 60 | yes | OPERATE | pf = 0.000 leading
55 | Power factor | Quick CMC | points | 4 | Below minimum current | Same angle, current dropped under the 0.30 ×FLA supervision |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 1.0800@50.6 | 1.0800@-69.4 | 1.0800@170.6 | 60 | yes | BLOCKED | pf = 0.635 leading
32 | Underpower / reverse power | Quick CMC | points | 1 | Below threshold — load lost | 85% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.6598@0.0 | 0.6598@-120.0 | 0.6598@120.0 | 60 | yes | OPERATE | 190.2 kW primary · 0.147 ×FLA
32 | Underpower / reverse power | Quick CMC | points | 2 | Above threshold | 115% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.8926@0.0 | 0.8926@-120.0 | 0.8926@120.0 | 60 | yes | RESTRAIN | 257.3 kW primary · 0.198 ×FLA
32 | Underpower / reverse power | Quick CMC | points | 3 | Timing at half pickup | Definite time |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.3881@0.0 | 0.3881@-120.0 | 0.3881@120.0 | 60 | yes | 5.00 s | 111.9 kW primary · 0.086 ×FLA
19 | Reduced voltage start transition | State Sequencer | sequence | 1 | Normal — stopped | No current, motor at rest | 1 | 1/4 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | READY
19 | Reduced voltage start transition | State Sequencer | sequence | 2 | Normal — on the reduced-voltage tap | Terminal voltage at 65% and current at 3.90 ×FLA — starting current falls roughly with the tap voltage | 1 | 2/4 | 6 | 45.033@0.0 | 45.033@-120.0 | 45.033@120.0 | 17.5500@-27.1 | 17.5500@-147.1 | 17.5500@92.9 | 60 | yes | NO TRIP | Inside the 10.0 s tap limit
19 | Reduced voltage start transition | State Sequencer | sequence | 3 | Normal — transition to full voltage | Voltage restored to nominal, current drops through the 3.00 ×FLA transition level | 1 | 3/4 | 3 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 12.1500@-27.1 | 12.1500@-147.1 | 12.1500@92.9 | 60 | yes | TRANSITION | Transition contact operates
19 | Reduced voltage start transition | State Sequencer | sequence | 4 | Normal — running | Full load, start complete | 1 | 4/4 | 8 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.5000@-27.1 | 4.5000@-147.1 | 4.5000@92.9 | 60 | yes | RUNNING | Start supervision resets
19 | Reduced voltage start transition | State Sequencer | sequence | 5 | Failed — stopped | No current, motor at rest | 2 | 1/2 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | READY
19 | Reduced voltage start transition | State Sequencer | sequence | 6 | Failed — transition never happens | Held on the tap past the 10.0 s limit with current never falling below 3.00 ×FLA | 2 | 2/2 | 13 | 45.033@0.0 | 45.033@-120.0 | 45.033@120.0 | 17.5500@-27.1 | 17.5500@-147.1 | 17.5500@92.9 | 60 | yes | TRIP AT 10.0 s | The starter winding is not rated to sit there

## Channels
Function | Description | Group | TU module | Drive as | # | Test step | Run | State | State label | Dur s | Channel | Magnitude | Unit | Angle deg | Hz | Note | Expected | Expected — detail | Verdict
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Very long — 12.72 min from the curve | op
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Very long — 12.72 min from the curve | op
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Very long — 12.72 min from the curve | op
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L1 | 5.4337 | A | -27.13 | 60 |  | OPERATE | Very long — 12.72 min from the curve | op
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L2 | 5.4337 | A | -147.13 | 60 |  | OPERATE | Very long — 12.72 min from the curve | op
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L3 | 5.4337 | A | 92.87 | 60 |  | OPERATE | Very long — 12.72 min from the curve | op
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No accumulation | no
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No accumulation | no
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No accumulation | no
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L1 | 4.9162 | A | -27.13 | 60 |  | RESTRAIN | No accumulation | no
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L2 | 4.9162 | A | -147.13 | 60 |  | RESTRAIN | No accumulation | no
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L3 | 4.9162 | A | 92.87 | 60 |  | RESTRAIN | No accumulation | no
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 3 | Timing at 1.50 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 4.66 min | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 3 | Timing at 1.50 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 4.66 min | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 3 | Timing at 1.50 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 4.66 min | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 3 | Timing at 1.50 ×FLA |  |  |  |  | I L1 | 6.75 | A | -27.13 | 60 |  | 4.66 min | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 3 | Timing at 1.50 ×FLA |  |  |  |  | I L2 | 6.75 | A | -147.13 | 60 |  | 4.66 min | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 3 | Timing at 1.50 ×FLA |  |  |  |  | I L3 | 6.75 | A | 92.87 | 60 |  | 4.66 min | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 4 | Timing at 2.00 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 116.5 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 4 | Timing at 2.00 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 116.5 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 4 | Timing at 2.00 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 116.5 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 4 | Timing at 2.00 ×FLA |  |  |  |  | I L1 | 9 | A | -27.13 | 60 |  | 116.5 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 4 | Timing at 2.00 ×FLA |  |  |  |  | I L2 | 9 | A | -147.13 | 60 |  | 116.5 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 4 | Timing at 2.00 ×FLA |  |  |  |  | I L3 | 9 | A | 92.87 | 60 |  | 116.5 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 5 | Timing at 3.00 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 43.7 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 5 | Timing at 3.00 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 43.7 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 5 | Timing at 3.00 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 43.7 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 5 | Timing at 3.00 ×FLA |  |  |  |  | I L1 | 13.5 | A | -27.13 | 60 |  | 43.7 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 5 | Timing at 3.00 ×FLA |  |  |  |  | I L2 | 13.5 | A | -147.13 | 60 |  | 43.7 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 5 | Timing at 3.00 ×FLA |  |  |  |  | I L3 | 13.5 | A | 92.87 | 60 |  | 43.7 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 6 | Timing at 4.00 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 23.3 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 6 | Timing at 4.00 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 23.3 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 6 | Timing at 4.00 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 23.3 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 6 | Timing at 4.00 ×FLA |  |  |  |  | I L1 | 18 | A | -27.13 | 60 |  | 23.3 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 6 | Timing at 4.00 ×FLA |  |  |  |  | I L2 | 18 | A | -147.13 | 60 |  | 23.3 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 6 | Timing at 4.00 ×FLA |  |  |  |  | I L3 | 18 | A | 92.87 | 60 |  | 23.3 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 7 | Timing at 6.00 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 9.99 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 7 | Timing at 6.00 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 9.99 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 7 | Timing at 6.00 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 9.99 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 7 | Timing at 6.00 ×FLA |  |  |  |  | I L1 | 27 | A | -27.13 | 60 |  | 9.99 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 7 | Timing at 6.00 ×FLA |  |  |  |  | I L2 | 27 | A | -147.13 | 60 |  | 9.99 s | From the cold overload curve | nu
49 | Thermal overload model | Thermal | Overcurrent | characteristic | 7 | Timing at 6.00 ×FLA |  |  |  |  | I L3 | 27 | A | 92.87 | 60 |  | 9.99 s | From the cold overload curve | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 1 | Accumulate at 2.0 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 87.4 s to alarm | Trip at 116.5 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 1 | Accumulate at 2.0 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 87.4 s to alarm | Trip at 116.5 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 1 | Accumulate at 2.0 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 87.4 s to alarm | Trip at 116.5 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 1 | Accumulate at 2.0 ×FLA |  |  |  |  | I L1 | 9 | A | -27.13 | 60 |  | 87.4 s to alarm | Trip at 116.5 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 1 | Accumulate at 2.0 ×FLA |  |  |  |  | I L2 | 9 | A | -147.13 | 60 |  | 87.4 s to alarm | Trip at 116.5 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 1 | Accumulate at 2.0 ×FLA |  |  |  |  | I L3 | 9 | A | 92.87 | 60 |  | 87.4 s to alarm | Trip at 116.5 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 2 | Accumulate at 4.0 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 17.5 s to alarm | Trip at 23.3 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 2 | Accumulate at 4.0 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 17.5 s to alarm | Trip at 23.3 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 2 | Accumulate at 4.0 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 17.5 s to alarm | Trip at 23.3 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 2 | Accumulate at 4.0 ×FLA |  |  |  |  | I L1 | 18 | A | -27.13 | 60 |  | 17.5 s to alarm | Trip at 23.3 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 2 | Accumulate at 4.0 ×FLA |  |  |  |  | I L2 | 18 | A | -147.13 | 60 |  | 17.5 s to alarm | Trip at 23.3 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 2 | Accumulate at 4.0 ×FLA |  |  |  |  | I L3 | 18 | A | 92.87 | 60 |  | 17.5 s to alarm | Trip at 23.3 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 3 | Accumulate at 6.0 ×FLA |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 7.49 s to alarm | Trip at 9.99 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 3 | Accumulate at 6.0 ×FLA |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 7.49 s to alarm | Trip at 9.99 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 3 | Accumulate at 6.0 ×FLA |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 7.49 s to alarm | Trip at 9.99 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 3 | Accumulate at 6.0 ×FLA |  |  |  |  | I L1 | 27 | A | -27.13 | 60 |  | 7.49 s to alarm | Trip at 9.99 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 3 | Accumulate at 6.0 ×FLA |  |  |  |  | I L2 | 27 | A | -147.13 | 60 |  | 7.49 s to alarm | Trip at 9.99 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 3 | Accumulate at 6.0 ×FLA |  |  |  |  | I L3 | 27 | A | 92.87 | 60 |  | 7.49 s to alarm | Trip at 9.99 s · hold the current, do not interrupt it | nu
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 4 | Decay — 5 min stopped |  |  |  |  | V L1 | 0 | V | 0 | 60 |  | 84.6% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 4 | Decay — 5 min stopped |  |  |  |  | V L2 | 0 | V | -120 | 60 |  | 84.6% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 4 | Decay — 5 min stopped |  |  |  |  | V L3 | 0 | V | 120 | 60 |  | 84.6% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 4 | Decay — 5 min stopped |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | 84.6% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 4 | Decay — 5 min stopped |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 84.6% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 4 | Decay — 5 min stopped |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 84.6% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 5 | Decay — 15 min stopped |  |  |  |  | V L1 | 0 | V | 0 | 60 |  | 60.7% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 5 | Decay — 15 min stopped |  |  |  |  | V L2 | 0 | V | -120 | 60 |  | 60.7% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 5 | Decay — 15 min stopped |  |  |  |  | V L3 | 0 | V | 120 | 60 |  | 60.7% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 5 | Decay — 15 min stopped |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | 60.7% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 5 | Decay — 15 min stopped |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 60.7% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 5 | Decay — 15 min stopped |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 60.7% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 6 | Decay — 30 min stopped |  |  |  |  | V L1 | 0 | V | 0 | 60 |  | 36.8% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 6 | Decay — 30 min stopped |  |  |  |  | V L2 | 0 | V | -120 | 60 |  | 36.8% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 6 | Decay — 30 min stopped |  |  |  |  | V L3 | 0 | V | 120 | 60 |  | 36.8% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 6 | Decay — 30 min stopped |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | 36.8% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 6 | Decay — 30 min stopped |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 36.8% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 6 | Decay — 30 min stopped |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 36.8% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 7 | Decay — 60 min stopped |  |  |  |  | V L1 | 0 | V | 0 | 60 |  | 13.5% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 7 | Decay — 60 min stopped |  |  |  |  | V L2 | 0 | V | -120 | 60 |  | 13.5% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 7 | Decay — 60 min stopped |  |  |  |  | V L3 | 0 | V | 120 | 60 |  | 13.5% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 7 | Decay — 60 min stopped |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | 13.5% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 7 | Decay — 60 min stopped |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 13.5% remaining | Restart permitted below 100% | op
49TC | Thermal capacity and lockout | Thermal | Quick CMC | points | 7 | Decay — 60 min stopped |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 13.5% remaining | Restart permitted below 100% | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 1 | Stopped | 1 | 1/3 | Stopped | 3 | V L1 | 0 | V | 0 | 60 |  | READY | Start supervision idle | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 1 | Stopped | 1 | 1/3 | Stopped | 3 | V L2 | 0 | V | -120 | 60 |  | READY | Start supervision idle | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 1 | Stopped | 1 | 1/3 | Stopped | 3 | V L3 | 0 | V | 120 | 60 |  | READY | Start supervision idle | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 1 | Stopped | 1 | 1/3 | Stopped | 3 | I L1 | 0 | A | 0 | 60 |  | READY | Start supervision idle | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 1 | Stopped | 1 | 1/3 | Stopped | 3 | I L2 | 0 | A | 0 | 60 |  | READY | Start supervision idle | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 1 | Stopped | 1 | 1/3 | Stopped | 3 | I L3 | 0 | A | 0 | 60 |  | READY | Start supervision idle | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 2 | Successful start — acceleration | 1 | 2/3 | Accelerating | 8 | V L1 | 58.89 | V | 0 | 60 |  | NO TRIP | Inside the 10.0 s limit | no
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 2 | Successful start — acceleration | 1 | 2/3 | Accelerating | 8 | V L2 | 58.89 | V | -120 | 60 |  | NO TRIP | Inside the 10.0 s limit | no
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 2 | Successful start — acceleration | 1 | 2/3 | Accelerating | 8 | V L3 | 58.89 | V | 120 | 60 |  | NO TRIP | Inside the 10.0 s limit | no
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 2 | Successful start — acceleration | 1 | 2/3 | Accelerating | 8 | I L1 | 27 | A | -27.13 | 60 |  | NO TRIP | Inside the 10.0 s limit | no
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 2 | Successful start — acceleration | 1 | 2/3 | Accelerating | 8 | I L2 | 27 | A | -147.13 | 60 |  | NO TRIP | Inside the 10.0 s limit | no
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 2 | Successful start — acceleration | 1 | 2/3 | Accelerating | 8 | I L3 | 27 | A | 92.87 | 60 |  | NO TRIP | Inside the 10.0 s limit | no
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 3 | Successful start — running | 1 | 3/3 | Running | 10 | V L1 | 69.282 | V | 0 | 60 |  | START COMPLETE | Acceleration timer resets | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 3 | Successful start — running | 1 | 3/3 | Running | 10 | V L2 | 69.282 | V | -120 | 60 |  | START COMPLETE | Acceleration timer resets | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 3 | Successful start — running | 1 | 3/3 | Running | 10 | V L3 | 69.282 | V | 120 | 60 |  | START COMPLETE | Acceleration timer resets | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 3 | Successful start — running | 1 | 3/3 | Running | 10 | I L1 | 4.5 | A | -27.13 | 60 |  | START COMPLETE | Acceleration timer resets | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 3 | Successful start — running | 1 | 3/3 | Running | 10 | I L2 | 4.5 | A | -147.13 | 60 |  | START COMPLETE | Acceleration timer resets | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 3 | Successful start — running | 1 | 3/3 | Running | 10 | I L3 | 4.5 | A | 92.87 | 60 |  | START COMPLETE | Acceleration timer resets | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 4 | Stalled start — stopped | 2 | 1/2 | Stopped | 3 | V L1 | 0 | V | 0 | 60 |  | READY |  | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 4 | Stalled start — stopped | 2 | 1/2 | Stopped | 3 | V L2 | 0 | V | -120 | 60 |  | READY |  | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 4 | Stalled start — stopped | 2 | 1/2 | Stopped | 3 | V L3 | 0 | V | 120 | 60 |  | READY |  | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 4 | Stalled start — stopped | 2 | 1/2 | Stopped | 3 | I L1 | 0 | A | 0 | 60 |  | READY |  | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 4 | Stalled start — stopped | 2 | 1/2 | Stopped | 3 | I L2 | 0 | A | 0 | 60 |  | READY |  | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 4 | Stalled start — stopped | 2 | 1/2 | Stopped | 3 | I L3 | 0 | A | 0 | 60 |  | READY |  | nu
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 5 | Stalled start — current never drops | 2 | 2/2 | Stalled | 13 | V L1 | 58.89 | V | 0 | 60 |  | TRIP AT 10.0 s | Incomplete sequence, or the thermal curve first — see the note below | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 5 | Stalled start — current never drops | 2 | 2/2 | Stalled | 13 | V L2 | 58.89 | V | -120 | 60 |  | TRIP AT 10.0 s | Incomplete sequence, or the thermal curve first — see the note below | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 5 | Stalled start — current never drops | 2 | 2/2 | Stalled | 13 | V L3 | 58.89 | V | 120 | 60 |  | TRIP AT 10.0 s | Incomplete sequence, or the thermal curve first — see the note below | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 5 | Stalled start — current never drops | 2 | 2/2 | Stalled | 13 | I L1 | 27 | A | -27.13 | 60 |  | TRIP AT 10.0 s | Incomplete sequence, or the thermal curve first — see the note below | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 5 | Stalled start — current never drops | 2 | 2/2 | Stalled | 13 | I L2 | 27 | A | -147.13 | 60 |  | TRIP AT 10.0 s | Incomplete sequence, or the thermal curve first — see the note below | op
48 | Acceleration time / incomplete sequence | Starting | State Sequencer | sequence | 5 | Stalled start — current never drops | 2 | 2/2 | Stalled | 13 | I L3 | 27 | A | 92.87 | 60 |  | TRIP AT 10.0 s | Incomplete sequence, or the thermal curve first — see the note below | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 1 | Jam — above pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | TRIP | Operate after 1.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 1 | Jam — above pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | TRIP | Operate after 1.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 1 | Jam — above pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | TRIP | Operate after 1.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 1 | Jam — above pickup |  |  |  |  | I L1 | 11.8125 | A | -27.13 | 60 |  | TRIP | Operate after 1.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 1 | Jam — above pickup |  |  |  |  | I L2 | 11.8125 | A | -147.13 | 60 |  | TRIP | Operate after 1.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 1 | Jam — above pickup |  |  |  |  | I L3 | 11.8125 | A | 92.87 | 60 |  | TRIP | Operate after 1.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 2 | Jam — below pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | No operation | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 2 | Jam — below pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | No operation | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 2 | Jam — below pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | No operation | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 2 | Jam — below pickup |  |  |  |  | I L1 | 10.6875 | A | -27.13 | 60 |  | NO TRIP | No operation | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 2 | Jam — below pickup |  |  |  |  | I L2 | 10.6875 | A | -147.13 | 60 |  | NO TRIP | No operation | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 2 | Jam — below pickup |  |  |  |  | I L3 | 10.6875 | A | 92.87 | 60 |  | NO TRIP | No operation | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 3 | Locked rotor — above pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | TRIP | Operate after 2.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 3 | Locked rotor — above pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | TRIP | Operate after 2.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 3 | Locked rotor — above pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | TRIP | Operate after 2.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 3 | Locked rotor — above pickup |  |  |  |  | I L1 | 21.2625 | A | -27.13 | 60 |  | TRIP | Operate after 2.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 3 | Locked rotor — above pickup |  |  |  |  | I L2 | 21.2625 | A | -147.13 | 60 |  | TRIP | Operate after 2.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 3 | Locked rotor — above pickup |  |  |  |  | I L3 | 21.2625 | A | 92.87 | 60 |  | TRIP | Operate after 2.00 s | op
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 4 | Jam blocked during start |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | JAM BLOCKED | A normal start must not look like a jam | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 4 | Jam blocked during start |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | JAM BLOCKED | A normal start must not look like a jam | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 4 | Jam blocked during start |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | JAM BLOCKED | A normal start must not look like a jam | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 4 | Jam blocked during start |  |  |  |  | I L1 | 27 | A | -27.13 | 60 |  | JAM BLOCKED | A normal start must not look like a jam | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 4 | Jam blocked during start |  |  |  |  | I L2 | 27 | A | -147.13 | 60 |  | JAM BLOCKED | A normal start must not look like a jam | no
51LR | Locked rotor and mechanical jam | Starting | Overcurrent | pickup+time | 4 | Jam blocked during start |  |  |  |  | I L3 | 27 | A | 92.87 | 60 |  | JAM BLOCKED | A normal start must not look like a jam | no
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 1 | Start 1 of 3 | 1 | 1/10 | Start 1 | 8 | V L1 | 58.89 | V | 0 | 60 |  | PERMITTED | Counter advances to 1 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 1 | Start 1 of 3 | 1 | 1/10 | Start 1 | 8 | V L2 | 58.89 | V | -120 | 60 |  | PERMITTED | Counter advances to 1 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 1 | Start 1 of 3 | 1 | 1/10 | Start 1 | 8 | V L3 | 58.89 | V | 120 | 60 |  | PERMITTED | Counter advances to 1 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 1 | Start 1 of 3 | 1 | 1/10 | Start 1 | 8 | I L1 | 27 | A | -27.13 | 60 |  | PERMITTED | Counter advances to 1 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 1 | Start 1 of 3 | 1 | 1/10 | Start 1 | 8 | I L2 | 27 | A | -147.13 | 60 |  | PERMITTED | Counter advances to 1 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 1 | Start 1 of 3 | 1 | 1/10 | Start 1 | 8 | I L3 | 27 | A | 92.87 | 60 |  | PERMITTED | Counter advances to 1 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 2 | Run after start 1 | 1 | 2/10 | Run 1 | 30 | V L1 | 69.282 | V | 0 | 60 |  | RUNNING | 2 starts left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 2 | Run after start 1 | 1 | 2/10 | Run 1 | 30 | V L2 | 69.282 | V | -120 | 60 |  | RUNNING | 2 starts left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 2 | Run after start 1 | 1 | 2/10 | Run 1 | 30 | V L3 | 69.282 | V | 120 | 60 |  | RUNNING | 2 starts left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 2 | Run after start 1 | 1 | 2/10 | Run 1 | 30 | I L1 | 4.5 | A | -27.13 | 60 |  | RUNNING | 2 starts left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 2 | Run after start 1 | 1 | 2/10 | Run 1 | 30 | I L2 | 4.5 | A | -147.13 | 60 |  | RUNNING | 2 starts left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 2 | Run after start 1 | 1 | 2/10 | Run 1 | 30 | I L3 | 4.5 | A | 92.87 | 60 |  | RUNNING | 2 starts left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 3 | Stopped after start 1 | 1 | 3/10 | Stopped 1 | 5 | V L1 | 0 | V | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 3 | Stopped after start 1 | 1 | 3/10 | Stopped 1 | 5 | V L2 | 0 | V | -120 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 3 | Stopped after start 1 | 1 | 3/10 | Stopped 1 | 5 | V L3 | 0 | V | 120 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 3 | Stopped after start 1 | 1 | 3/10 | Stopped 1 | 5 | I L1 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 3 | Stopped after start 1 | 1 | 3/10 | Stopped 1 | 5 | I L2 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 3 | Stopped after start 1 | 1 | 3/10 | Stopped 1 | 5 | I L3 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 4 | Start 2 of 3 | 1 | 4/10 | Start 2 | 8 | V L1 | 58.89 | V | 0 | 60 |  | PERMITTED | Counter advances to 2 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 4 | Start 2 of 3 | 1 | 4/10 | Start 2 | 8 | V L2 | 58.89 | V | -120 | 60 |  | PERMITTED | Counter advances to 2 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 4 | Start 2 of 3 | 1 | 4/10 | Start 2 | 8 | V L3 | 58.89 | V | 120 | 60 |  | PERMITTED | Counter advances to 2 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 4 | Start 2 of 3 | 1 | 4/10 | Start 2 | 8 | I L1 | 27 | A | -27.13 | 60 |  | PERMITTED | Counter advances to 2 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 4 | Start 2 of 3 | 1 | 4/10 | Start 2 | 8 | I L2 | 27 | A | -147.13 | 60 |  | PERMITTED | Counter advances to 2 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 4 | Start 2 of 3 | 1 | 4/10 | Start 2 | 8 | I L3 | 27 | A | 92.87 | 60 |  | PERMITTED | Counter advances to 2 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 5 | Run after start 2 | 1 | 5/10 | Run 2 | 30 | V L1 | 69.282 | V | 0 | 60 |  | RUNNING | 1 start left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 5 | Run after start 2 | 1 | 5/10 | Run 2 | 30 | V L2 | 69.282 | V | -120 | 60 |  | RUNNING | 1 start left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 5 | Run after start 2 | 1 | 5/10 | Run 2 | 30 | V L3 | 69.282 | V | 120 | 60 |  | RUNNING | 1 start left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 5 | Run after start 2 | 1 | 5/10 | Run 2 | 30 | I L1 | 4.5 | A | -27.13 | 60 |  | RUNNING | 1 start left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 5 | Run after start 2 | 1 | 5/10 | Run 2 | 30 | I L2 | 4.5 | A | -147.13 | 60 |  | RUNNING | 1 start left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 5 | Run after start 2 | 1 | 5/10 | Run 2 | 30 | I L3 | 4.5 | A | 92.87 | 60 |  | RUNNING | 1 start left in the hour | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 6 | Stopped after start 2 | 1 | 6/10 | Stopped 2 | 5 | V L1 | 0 | V | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 6 | Stopped after start 2 | 1 | 6/10 | Stopped 2 | 5 | V L2 | 0 | V | -120 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 6 | Stopped after start 2 | 1 | 6/10 | Stopped 2 | 5 | V L3 | 0 | V | 120 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 6 | Stopped after start 2 | 1 | 6/10 | Stopped 2 | 5 | I L1 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 6 | Stopped after start 2 | 1 | 6/10 | Stopped 2 | 5 | I L2 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 6 | Stopped after start 2 | 1 | 6/10 | Stopped 2 | 5 | I L3 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 7 | Start 3 of 3 | 1 | 7/10 | Start 3 | 8 | V L1 | 58.89 | V | 0 | 60 |  | PERMITTED | Counter advances to 3 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 7 | Start 3 of 3 | 1 | 7/10 | Start 3 | 8 | V L2 | 58.89 | V | -120 | 60 |  | PERMITTED | Counter advances to 3 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 7 | Start 3 of 3 | 1 | 7/10 | Start 3 | 8 | V L3 | 58.89 | V | 120 | 60 |  | PERMITTED | Counter advances to 3 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 7 | Start 3 of 3 | 1 | 7/10 | Start 3 | 8 | I L1 | 27 | A | -27.13 | 60 |  | PERMITTED | Counter advances to 3 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 7 | Start 3 of 3 | 1 | 7/10 | Start 3 | 8 | I L2 | 27 | A | -147.13 | 60 |  | PERMITTED | Counter advances to 3 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 7 | Start 3 of 3 | 1 | 7/10 | Start 3 | 8 | I L3 | 27 | A | 92.87 | 60 |  | PERMITTED | Counter advances to 3 | op
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 8 | Run after start 3 | 1 | 8/10 | Run 3 | 30 | V L1 | 69.282 | V | 0 | 60 |  | RUNNING | No starts left | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 8 | Run after start 3 | 1 | 8/10 | Run 3 | 30 | V L2 | 69.282 | V | -120 | 60 |  | RUNNING | No starts left | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 8 | Run after start 3 | 1 | 8/10 | Run 3 | 30 | V L3 | 69.282 | V | 120 | 60 |  | RUNNING | No starts left | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 8 | Run after start 3 | 1 | 8/10 | Run 3 | 30 | I L1 | 4.5 | A | -27.13 | 60 |  | RUNNING | No starts left | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 8 | Run after start 3 | 1 | 8/10 | Run 3 | 30 | I L2 | 4.5 | A | -147.13 | 60 |  | RUNNING | No starts left | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 8 | Run after start 3 | 1 | 8/10 | Run 3 | 30 | I L3 | 4.5 | A | 92.87 | 60 |  | RUNNING | No starts left | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 9 | Stopped after start 3 | 1 | 9/10 | Stopped 3 | 5 | V L1 | 0 | V | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 9 | Stopped after start 3 | 1 | 9/10 | Stopped 3 | 5 | V L2 | 0 | V | -120 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 9 | Stopped after start 3 | 1 | 9/10 | Stopped 3 | 5 | V L3 | 0 | V | 120 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 9 | Stopped after start 3 | 1 | 9/10 | Stopped 3 | 5 | I L1 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 9 | Stopped after start 3 | 1 | 9/10 | Stopped 3 | 5 | I L2 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 9 | Stopped after start 3 | 1 | 9/10 | Stopped 3 | 5 | I L3 | 0 | A | 0 | 60 |  | STOPPED | Restart delay of 60.0 s begins | nu
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 10 | Start 4 — refused | 1 | 10/10 | Blocked | 60 | V L1 | 58.89 | V | 0 | 60 |  | START INHIBITED | The relay must block the close, not trip after it | no
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 10 | Start 4 — refused | 1 | 10/10 | Blocked | 60 | V L2 | 58.89 | V | -120 | 60 |  | START INHIBITED | The relay must block the close, not trip after it | no
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 10 | Start 4 — refused | 1 | 10/10 | Blocked | 60 | V L3 | 58.89 | V | 120 | 60 |  | START INHIBITED | The relay must block the close, not trip after it | no
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 10 | Start 4 — refused | 1 | 10/10 | Blocked | 60 | I L1 | 27 | A | -27.13 | 60 |  | START INHIBITED | The relay must block the close, not trip after it | no
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 10 | Start 4 — refused | 1 | 10/10 | Blocked | 60 | I L2 | 27 | A | -147.13 | 60 |  | START INHIBITED | The relay must block the close, not trip after it | no
66 | Starts per hour / time between starts | Starting | State Sequencer | sequence | 10 | Start 4 — refused | 1 | 10/10 | Blocked | 60 | I L3 | 27 | A | 92.87 | 60 |  | START INHIBITED | The relay must block the close, not trip after it | no
46 | Current unbalance | Current | Overcurrent | characteristic | 1 | Ratio — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 5.00 s | op
46 | Current unbalance | Current | Overcurrent | characteristic | 1 | Ratio — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 5.00 s | op
46 | Current unbalance | Current | Overcurrent | characteristic | 1 | Ratio — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 5.00 s | op
46 | Current unbalance | Current | Overcurrent | characteristic | 1 | Ratio — above threshold |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | OPERATE | Operate after 5.00 s | op
46 | Current unbalance | Current | Overcurrent | characteristic | 1 | Ratio — above threshold |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | OPERATE | Operate after 5.00 s | op
46 | Current unbalance | Current | Overcurrent | characteristic | 1 | Ratio — above threshold |  |  |  |  | I L3 | 2.588 | A | 92.87 | 60 | reduced to 57.5% of the others | OPERATE | Operate after 5.00 s | op
46 | Current unbalance | Current | Overcurrent | characteristic | 2 | Ratio — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
46 | Current unbalance | Current | Overcurrent | characteristic | 2 | Ratio — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
46 | Current unbalance | Current | Overcurrent | characteristic | 2 | Ratio — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
46 | Current unbalance | Current | Overcurrent | characteristic | 2 | Ratio — below threshold |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | RESTRAIN | No operation | no
46 | Current unbalance | Current | Overcurrent | characteristic | 2 | Ratio — below threshold |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | RESTRAIN | No operation | no
46 | Current unbalance | Current | Overcurrent | characteristic | 2 | Ratio — below threshold |  |  |  |  | I L3 | 2.8943 | A | 92.87 | 60 | reduced to 64.3% of the others | RESTRAIN | No operation | no
46 | Current unbalance | Current | Overcurrent | characteristic | 3 | Alarm threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | ALARM ONLY | Alarm asserts, trip does not | wn
46 | Current unbalance | Current | Overcurrent | characteristic | 3 | Alarm threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | ALARM ONLY | Alarm asserts, trip does not | wn
46 | Current unbalance | Current | Overcurrent | characteristic | 3 | Alarm threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | ALARM ONLY | Alarm asserts, trip does not | wn
46 | Current unbalance | Current | Overcurrent | characteristic | 3 | Alarm threshold |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | ALARM ONLY | Alarm asserts, trip does not | wn
46 | Current unbalance | Current | Overcurrent | characteristic | 3 | Alarm threshold |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | ALARM ONLY | Alarm asserts, trip does not | wn
46 | Current unbalance | Current | Overcurrent | characteristic | 3 | Alarm threshold |  |  |  |  | I L3 | 3.2727 | A | 92.87 | 60 | reduced to 72.7% of the others | ALARM ONLY | Alarm asserts, trip does not | wn
46 | Current unbalance | Current | Overcurrent | characteristic | 4 | Single phasing |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | I2/I1 = 50%, the ceiling for this method | op
46 | Current unbalance | Current | Overcurrent | characteristic | 4 | Single phasing |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | I2/I1 = 50%, the ceiling for this method | op
46 | Current unbalance | Current | Overcurrent | characteristic | 4 | Single phasing |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | I2/I1 = 50%, the ceiling for this method | op
46 | Current unbalance | Current | Overcurrent | characteristic | 4 | Single phasing |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | OPERATE | I2/I1 = 50%, the ceiling for this method | op
46 | Current unbalance | Current | Overcurrent | characteristic | 4 | Single phasing |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | OPERATE | I2/I1 = 50%, the ceiling for this method | op
46 | Current unbalance | Current | Overcurrent | characteristic | 4 | Single phasing |  |  |  |  | I L3 | 0 | A | 92.87 | 60 | reduced to 0.0% of the others | OPERATE | I2/I1 = 50%, the ceiling for this method | op
46 | Current unbalance | Current | Overcurrent | characteristic | 5 | Reverse rotation |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | I2/I1 is undefined with I1 at zero; the element should see full unbalance | op
46 | Current unbalance | Current | Overcurrent | characteristic | 5 | Reverse rotation |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | I2/I1 is undefined with I1 at zero; the element should see full unbalance | op
46 | Current unbalance | Current | Overcurrent | characteristic | 5 | Reverse rotation |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | I2/I1 is undefined with I1 at zero; the element should see full unbalance | op
46 | Current unbalance | Current | Overcurrent | characteristic | 5 | Reverse rotation |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | OPERATE | I2/I1 is undefined with I1 at zero; the element should see full unbalance | op
46 | Current unbalance | Current | Overcurrent | characteristic | 5 | Reverse rotation |  |  |  |  | I L2 | 4.5 | A | 92.87 | 60 |  | OPERATE | I2/I1 is undefined with I1 at zero; the element should see full unbalance | op
46 | Current unbalance | Current | Overcurrent | characteristic | 5 | Reverse rotation |  |  |  |  | I L3 | 4.5 | A | -147.13 | 60 |  | OPERATE | I2/I1 is undefined with I1 at zero; the element should see full unbalance | op
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | TRIP | Operate after 5.00 s | op
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | TRIP | Operate after 5.00 s | op
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | TRIP | Operate after 5.00 s | op
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L1 | 2.565 | A | -27.13 | 60 |  | TRIP | Operate after 5.00 s | op
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L2 | 2.565 | A | -147.13 | 60 |  | TRIP | Operate after 5.00 s | op
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L3 | 2.565 | A | 92.87 | 60 |  | TRIP | Operate after 5.00 s | op
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | No operation | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | No operation | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | No operation | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L1 | 2.835 | A | -27.13 | 60 |  | NO TRIP | No operation | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L2 | 2.835 | A | -147.13 | 60 |  | NO TRIP | No operation | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L3 | 2.835 | A | 92.87 | 60 |  | NO TRIP | No operation | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 5.00 s | Definite time | nu
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 5.00 s | Definite time | nu
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 5.00 s | Definite time | nu
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | I L1 | 1.35 | A | -27.13 | 60 |  | 5.00 s | Definite time | nu
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | I L2 | 1.35 | A | -147.13 | 60 |  | 5.00 s | Definite time | nu
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | I L3 | 1.35 | A | 92.87 | 60 |  | 5.00 s | Definite time | nu
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 4 | Motor stopped |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | Element supervised by the run status | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 4 | Motor stopped |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | Element supervised by the run status | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 4 | Motor stopped |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | Element supervised by the run status | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 4 | Motor stopped |  |  |  |  | I L1 | 0 | A | -27.13 | 60 |  | NO TRIP | Element supervised by the run status | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 4 | Motor stopped |  |  |  |  | I L2 | 0 | A | -147.13 | 60 |  | NO TRIP | Element supervised by the run status | no
37 | Undercurrent / loss of load | Current | Overcurrent | pickup+time | 4 | Motor stopped |  |  |  |  | I L3 | 0 | A | 92.87 | 60 |  | NO TRIP | Element supervised by the run status | no
87M | Motor differential | Current | Quick CMC | points | 1 | Sensitivity — above pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.03 s | op
87M | Motor differential | Current | Quick CMC | points | 1 | Sensitivity — above pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.03 s | op
87M | Motor differential | Current | Quick CMC | points | 1 | Sensitivity — above pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.03 s | op
87M | Motor differential | Current | Quick CMC | points | 1 | Sensitivity — above pickup |  |  |  |  | I L1 | 0.022 | A | 0 | 60 | single conductor through the differential window | OPERATE | Operate within 0.03 s | op
87M | Motor differential | Current | Quick CMC | points | 2 | Sensitivity — below pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
87M | Motor differential | Current | Quick CMC | points | 2 | Sensitivity — below pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
87M | Motor differential | Current | Quick CMC | points | 2 | Sensitivity — below pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
87M | Motor differential | Current | Quick CMC | points | 2 | Sensitivity — below pickup |  |  |  |  | I L1 | 0.018 | A | 0 | 60 | single conductor through the differential window | RESTRAIN | No operation | no
87M | Motor differential | Current | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | A balanced set through the window sums to zero | no
87M | Motor differential | Current | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | A balanced set through the window sums to zero | no
87M | Motor differential | Current | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | A balanced set through the window sums to zero | no
87M | Motor differential | Current | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I L1 | 18 | A | 0 | 60 |  | RESTRAIN | A balanced set through the window sums to zero | no
87M | Motor differential | Current | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I L2 | 18 | A | -120 | 60 |  | RESTRAIN | A balanced set through the window sums to zero | no
87M | Motor differential | Current | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I L3 | 18 | A | 120 | 60 |  | RESTRAIN | A balanced set through the window sums to zero | no
50P | Short circuit | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Short circuit | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Short circuit | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Short circuit | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 37.8 | A | -30 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Short circuit | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Short circuit | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Short circuit | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50P | Short circuit | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50P | Short circuit | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50P | Short circuit | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 34.2 | A | -30 | 60 |  | RESTRAIN | No operation | no
50P | Short circuit | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Short circuit | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Short circuit | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50P | Short circuit | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50P | Short circuit | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50P | Short circuit | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 72 | A | -30 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50P | Short circuit | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50P | Short circuit | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0.525 | A | -30 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0.475 | A | -30 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 1 | A | -30 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50G | Ground instantaneous | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Current | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Current | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Current | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0.315 | A | -30 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Current | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Current | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Current | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Current | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Current | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Current | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0.285 | A | -30 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Current | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Current | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Current | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 2.01 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 2.01 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 2.01 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 0.6 | A | -30 | 60 |  | 2.01 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 2.01 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 2.01 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 1.26 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 1.26 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 1.26 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L1 | 0.9 | A | -30 | 60 |  | 1.26 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 1.26 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 1.26 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.86 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.86 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.86 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L1 | 1.5 | A | -30 | 60 |  | 0.86 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.86 s | Predicted from the curve equation | nu
51G | Ground time OC | Current | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.86 s | Predicted from the curve equation | nu
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0.0525 | A | -30 | 60 |  | OPERATE | Operate within 0.05 s | op
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0.0475 | A | -30 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 0.1 | A | -30 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50SG | Sensitive ground | Current | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.05 s | Measured from application of current to trip | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | I L1 | 0.945 | A | -27.13 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | I L2 | 0.945 | A | -147.13 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | I L3 | 0.945 | A | 92.87 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | I L1 | 0.855 | A | -27.13 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | I L2 | 0.855 | A | -147.13 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | I L3 | 0.855 | A | 92.87 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.10 s | Timer 1 | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.10 s | Timer 1 | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.10 s | Timer 1 | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L1 | 2.7 | A | -27.13 | 60 |  | 0.10 s | Timer 1 | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L2 | 2.7 | A | -147.13 | 60 |  | 0.10 s | Timer 1 | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L3 | 2.7 | A | 92.87 | 60 |  | 0.10 s | Timer 1 | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 4 | Upstream trip timing |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.25 s | Timer 2 — trips the feeding breaker | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 4 | Upstream trip timing |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.25 s | Timer 2 — trips the feeding breaker | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 4 | Upstream trip timing |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.25 s | Timer 2 — trips the feeding breaker | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 4 | Upstream trip timing |  |  |  |  | I L1 | 2.7 | A | -27.13 | 60 |  | 0.25 s | Timer 2 — trips the feeding breaker | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 4 | Upstream trip timing |  |  |  |  | I L2 | 2.7 | A | -147.13 | 60 |  | 0.25 s | Timer 2 — trips the feeding breaker | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 4 | Upstream trip timing |  |  |  |  | I L3 | 2.7 | A | 92.87 | 60 |  | 0.25 s | Timer 2 — trips the feeding breaker | nu
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L1 | 0 | A | -27.13 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L2 | 0 | A | -147.13 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker or contactor failure | Current | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L3 | 0 | A | 92.87 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L1 | 52.654 | V | 0 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L2 | 52.654 | V | -120 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L3 | 52.654 | V | 120 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L1 | 58.197 | V | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L2 | 58.197 | V | -120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L3 | 58.197 | V | 120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× pickup |  |  |  |  | V L1 | 27.713 | V | 0 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× pickup |  |  |  |  | V L2 | 27.713 | V | -120 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× pickup |  |  |  |  | V L3 | 27.713 | V | 120 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× pickup |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× pickup |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× pickup |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L1 | 4 | V | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L2 | 4 | V | -120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L3 | 4 | V | 120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 5 | During a start |  |  |  |  | V L1 | 55.426 | V | 0 | 60 |  | NO TRIP | A healthy start must not trip on undervoltage | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 5 | During a start |  |  |  |  | V L2 | 55.426 | V | -120 | 60 |  | NO TRIP | A healthy start must not trip on undervoltage | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 5 | During a start |  |  |  |  | V L3 | 55.426 | V | 120 | 60 |  | NO TRIP | A healthy start must not trip on undervoltage | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 5 | During a start |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | NO TRIP | A healthy start must not trip on undervoltage | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 5 | During a start |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | NO TRIP | A healthy start must not trip on undervoltage | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 5 | During a start |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | NO TRIP | A healthy start must not trip on undervoltage | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 80.021 | V | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 80.021 | V | -120 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 80.021 | V | 120 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 72.4 | V | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 72.4 | V | -120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 72.4 | V | 120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | V L1 | 95.263 | V | 0 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | V L2 | 95.263 | V | -120 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | V L3 | 95.263 | V | 120 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | I L1 | 4.5 | A | -27.13 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | I L2 | 4.5 | A | -147.13 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | I L3 | 4.5 | A | 92.87 | 60 |  | 2.00 s | Definite time | nu
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L1 | 6.097 | V | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L2 | 6.097 | V | 120 | 60 |  | OPERATE | Operate after 2.00 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L3 | 6.097 | V | -120 | 60 |  | OPERATE | Operate after 2.00 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L1 | 4.988 | V | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L2 | 4.988 | V | 120 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L3 | 4.988 | V | -120 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Must block the start, not trip after it | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L2 | 69.282 | V | 120 | 60 |  | OPERATE | Must block the start, not trip after it | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L3 | 69.282 | V | -120 | 60 |  | OPERATE | Must block the start, not trip after it | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | Must block the start, not trip after it | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Must block the start, not trip after it | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Must block the start, not trip after it | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 56.9 |  | OPERATE | Operate after 2.00 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 56.9 |  | OPERATE | Operate after 2.00 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 56.9 |  | OPERATE | Operate after 2.00 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | I L1 | 0 | A | 0 | 56.9 |  | OPERATE | Operate after 2.00 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | I L2 | 0 | A | 0 | 56.9 |  | OPERATE | Operate after 2.00 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | I L3 | 0 | A | 0 | 56.9 |  | OPERATE | Operate after 2.00 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 57.1 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 57.1 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 57.1 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | I L1 | 0 | A | 0 | 57.1 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | I L2 | 0 | A | 0 | 57.1 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | I L3 | 0 | A | 0 | 57.1 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L1 | 69.282 | V | 0 | 56.9 |  | 2.00 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L2 | 69.282 | V | -120 | 56.9 |  | 2.00 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L3 | 69.282 | V | 120 | 56.9 |  | 2.00 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L1 | 0 | A | 0 | 56.9 |  | 2.00 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L2 | 0 | A | 0 | 56.9 |  | 2.00 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L3 | 0 | A | 0 | 56.9 |  | 2.00 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L1 | 24 | V | 0 | 56.9 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L2 | 24 | V | -120 | 56.9 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L3 | 24 | V | 120 | 56.9 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L1 | 0 | A | 0 | 56.9 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L2 | 0 | A | 0 | 56.9 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L3 | 0 | A | 0 | 56.9 |  | BLOCKED | Element inhibited | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 1 | Past the limit |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | pf = 0.635 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 1 | Past the limit |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | pf = 0.635 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 1 | Past the limit |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | pf = 0.635 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 1 | Past the limit |  |  |  |  | I L1 | 4.5 | A | 50.57 | 60 |  | OPERATE | pf = 0.635 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 1 | Past the limit |  |  |  |  | I L2 | 4.5 | A | -69.43 | 60 |  | OPERATE | pf = 0.635 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 1 | Past the limit |  |  |  |  | I L3 | 4.5 | A | 170.57 | 60 |  | OPERATE | pf = 0.635 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 2 | Short of the limit |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | pf = 0.760 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 2 | Short of the limit |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | pf = 0.760 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 2 | Short of the limit |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | pf = 0.760 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 2 | Short of the limit |  |  |  |  | I L1 | 4.5 | A | 40.57 | 60 |  | RESTRAIN | pf = 0.760 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 2 | Short of the limit |  |  |  |  | I L2 | 4.5 | A | -79.43 | 60 |  | RESTRAIN | pf = 0.760 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 2 | Short of the limit |  |  |  |  | I L3 | 4.5 | A | 160.57 | 60 |  | RESTRAIN | pf = 0.760 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 3 | Full VAR, no watts |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 3 | Full VAR, no watts |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 3 | Full VAR, no watts |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 3 | Full VAR, no watts |  |  |  |  | I L1 | 4.5 | A | 90 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 3 | Full VAR, no watts |  |  |  |  | I L2 | 4.5 | A | -30 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 3 | Full VAR, no watts |  |  |  |  | I L3 | 4.5 | A | -150 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Voltage & frequency | Quick CMC | points | 4 | Below minimum current |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | pf = 0.635 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 4 | Below minimum current |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | pf = 0.635 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 4 | Below minimum current |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | pf = 0.635 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 4 | Below minimum current |  |  |  |  | I L1 | 1.08 | A | 50.57 | 60 |  | BLOCKED | pf = 0.635 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 4 | Below minimum current |  |  |  |  | I L2 | 1.08 | A | -69.43 | 60 |  | BLOCKED | pf = 0.635 leading | no
55 | Power factor | Voltage & frequency | Quick CMC | points | 4 | Below minimum current |  |  |  |  | I L3 | 1.08 | A | 170.57 | 60 |  | BLOCKED | pf = 0.635 leading | no
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 1 | Below threshold — load lost |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | 190.2 kW primary · 0.147 ×FLA | op
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 1 | Below threshold — load lost |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | 190.2 kW primary · 0.147 ×FLA | op
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 1 | Below threshold — load lost |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | 190.2 kW primary · 0.147 ×FLA | op
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 1 | Below threshold — load lost |  |  |  |  | I L1 | 0.6598 | A | 0 | 60 |  | OPERATE | 190.2 kW primary · 0.147 ×FLA | op
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 1 | Below threshold — load lost |  |  |  |  | I L2 | 0.6598 | A | -120 | 60 |  | OPERATE | 190.2 kW primary · 0.147 ×FLA | op
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 1 | Below threshold — load lost |  |  |  |  | I L3 | 0.6598 | A | 120 | 60 |  | OPERATE | 190.2 kW primary · 0.147 ×FLA | op
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 2 | Above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | 257.3 kW primary · 0.198 ×FLA | no
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 2 | Above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | 257.3 kW primary · 0.198 ×FLA | no
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 2 | Above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | 257.3 kW primary · 0.198 ×FLA | no
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 2 | Above threshold |  |  |  |  | I L1 | 0.8926 | A | 0 | 60 |  | RESTRAIN | 257.3 kW primary · 0.198 ×FLA | no
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 2 | Above threshold |  |  |  |  | I L2 | 0.8926 | A | -120 | 60 |  | RESTRAIN | 257.3 kW primary · 0.198 ×FLA | no
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 2 | Above threshold |  |  |  |  | I L3 | 0.8926 | A | 120 | 60 |  | RESTRAIN | 257.3 kW primary · 0.198 ×FLA | no
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 3 | Timing at half pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 5.00 s | 111.9 kW primary · 0.086 ×FLA | nu
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 3 | Timing at half pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 5.00 s | 111.9 kW primary · 0.086 ×FLA | nu
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 3 | Timing at half pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 5.00 s | 111.9 kW primary · 0.086 ×FLA | nu
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 3 | Timing at half pickup |  |  |  |  | I L1 | 0.3881 | A | 0 | 60 |  | 5.00 s | 111.9 kW primary · 0.086 ×FLA | nu
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 3 | Timing at half pickup |  |  |  |  | I L2 | 0.3881 | A | -120 | 60 |  | 5.00 s | 111.9 kW primary · 0.086 ×FLA | nu
32 | Underpower / reverse power | Voltage & frequency | Quick CMC | points | 3 | Timing at half pickup |  |  |  |  | I L3 | 0.3881 | A | 120 | 60 |  | 5.00 s | 111.9 kW primary · 0.086 ×FLA | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 1 | Normal — stopped | 1 | 1/4 | Stopped | 3 | V L1 | 0 | V | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 1 | Normal — stopped | 1 | 1/4 | Stopped | 3 | V L2 | 0 | V | -120 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 1 | Normal — stopped | 1 | 1/4 | Stopped | 3 | V L3 | 0 | V | 120 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 1 | Normal — stopped | 1 | 1/4 | Stopped | 3 | I L1 | 0 | A | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 1 | Normal — stopped | 1 | 1/4 | Stopped | 3 | I L2 | 0 | A | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 1 | Normal — stopped | 1 | 1/4 | Stopped | 3 | I L3 | 0 | A | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 2 | Normal — on the reduced-voltage tap | 1 | 2/4 | On tap | 6 | V L1 | 45.033 | V | 0 | 60 |  | NO TRIP | Inside the 10.0 s tap limit | no
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 2 | Normal — on the reduced-voltage tap | 1 | 2/4 | On tap | 6 | V L2 | 45.033 | V | -120 | 60 |  | NO TRIP | Inside the 10.0 s tap limit | no
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 2 | Normal — on the reduced-voltage tap | 1 | 2/4 | On tap | 6 | V L3 | 45.033 | V | 120 | 60 |  | NO TRIP | Inside the 10.0 s tap limit | no
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 2 | Normal — on the reduced-voltage tap | 1 | 2/4 | On tap | 6 | I L1 | 17.55 | A | -27.13 | 60 |  | NO TRIP | Inside the 10.0 s tap limit | no
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 2 | Normal — on the reduced-voltage tap | 1 | 2/4 | On tap | 6 | I L2 | 17.55 | A | -147.13 | 60 |  | NO TRIP | Inside the 10.0 s tap limit | no
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 2 | Normal — on the reduced-voltage tap | 1 | 2/4 | On tap | 6 | I L3 | 17.55 | A | 92.87 | 60 |  | NO TRIP | Inside the 10.0 s tap limit | no
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 3 | Normal — transition to full voltage | 1 | 3/4 | Full volts | 3 | V L1 | 69.282 | V | 0 | 60 |  | TRANSITION | Transition contact operates | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 3 | Normal — transition to full voltage | 1 | 3/4 | Full volts | 3 | V L2 | 69.282 | V | -120 | 60 |  | TRANSITION | Transition contact operates | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 3 | Normal — transition to full voltage | 1 | 3/4 | Full volts | 3 | V L3 | 69.282 | V | 120 | 60 |  | TRANSITION | Transition contact operates | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 3 | Normal — transition to full voltage | 1 | 3/4 | Full volts | 3 | I L1 | 12.15 | A | -27.13 | 60 |  | TRANSITION | Transition contact operates | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 3 | Normal — transition to full voltage | 1 | 3/4 | Full volts | 3 | I L2 | 12.15 | A | -147.13 | 60 |  | TRANSITION | Transition contact operates | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 3 | Normal — transition to full voltage | 1 | 3/4 | Full volts | 3 | I L3 | 12.15 | A | 92.87 | 60 |  | TRANSITION | Transition contact operates | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 4 | Normal — running | 1 | 4/4 | Running | 8 | V L1 | 69.282 | V | 0 | 60 |  | RUNNING | Start supervision resets | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 4 | Normal — running | 1 | 4/4 | Running | 8 | V L2 | 69.282 | V | -120 | 60 |  | RUNNING | Start supervision resets | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 4 | Normal — running | 1 | 4/4 | Running | 8 | V L3 | 69.282 | V | 120 | 60 |  | RUNNING | Start supervision resets | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 4 | Normal — running | 1 | 4/4 | Running | 8 | I L1 | 4.5 | A | -27.13 | 60 |  | RUNNING | Start supervision resets | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 4 | Normal — running | 1 | 4/4 | Running | 8 | I L2 | 4.5 | A | -147.13 | 60 |  | RUNNING | Start supervision resets | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 4 | Normal — running | 1 | 4/4 | Running | 8 | I L3 | 4.5 | A | 92.87 | 60 |  | RUNNING | Start supervision resets | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 5 | Failed — stopped | 2 | 1/2 | Stopped | 3 | V L1 | 0 | V | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 5 | Failed — stopped | 2 | 1/2 | Stopped | 3 | V L2 | 0 | V | -120 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 5 | Failed — stopped | 2 | 1/2 | Stopped | 3 | V L3 | 0 | V | 120 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 5 | Failed — stopped | 2 | 1/2 | Stopped | 3 | I L1 | 0 | A | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 5 | Failed — stopped | 2 | 1/2 | Stopped | 3 | I L2 | 0 | A | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 5 | Failed — stopped | 2 | 1/2 | Stopped | 3 | I L3 | 0 | A | 0 | 60 |  | READY |  | nu
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 6 | Failed — transition never happens | 2 | 2/2 | Stuck on tap | 13 | V L1 | 45.033 | V | 0 | 60 |  | TRIP AT 10.0 s | The starter winding is not rated to sit there | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 6 | Failed — transition never happens | 2 | 2/2 | Stuck on tap | 13 | V L2 | 45.033 | V | -120 | 60 |  | TRIP AT 10.0 s | The starter winding is not rated to sit there | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 6 | Failed — transition never happens | 2 | 2/2 | Stuck on tap | 13 | V L3 | 45.033 | V | 120 | 60 |  | TRIP AT 10.0 s | The starter winding is not rated to sit there | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 6 | Failed — transition never happens | 2 | 2/2 | Stuck on tap | 13 | I L1 | 17.55 | A | -27.13 | 60 |  | TRIP AT 10.0 s | The starter winding is not rated to sit there | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 6 | Failed — transition never happens | 2 | 2/2 | Stuck on tap | 13 | I L2 | 17.55 | A | -147.13 | 60 |  | TRIP AT 10.0 s | The starter winding is not rated to sit there | op
19 | Reduced voltage start transition | Starting | State Sequencer | sequence | 6 | Failed — transition never happens | 2 | 2/2 | Stuck on tap | 13 | I L3 | 17.55 | A | 92.87 | 60 |  | TRIP AT 10.0 s | The starter winding is not rated to sit there | op

## Build guide
Building the 869 OCC in Test Universe
Assembles `869-MTR-steps.csv` and `869-MTR-channels.csv` into one Test Universe document —
20 elements, 92 steps. Build it once and save it as a template; the next motor is a
re-point of the test object.
Values below are for the tool's **sample** motor: 4.16 kV, 1500 hp induction, FLA 180 A,
service factor 1.15, 0.89 pf, 60 Hz, locked rotor 6 × FLA, LR withstand 20 s cold / 15 s
hot, nameplate acceleration 8 s, 3 starts per hour with 20 minutes between, CT 200:5,
core-balance ground CT 50:5, VT 4160:120 wye, differential by core balance. Enter your
real motor in `869.html` and re-run the generator.
---
1 · A motor plan is a thermal plan
Every other relay in this family is tested element by element in whatever order suits the
outage. The 869 is not, because the thermal model remembers. Section 5 is the part of this
guide that saves the day; read it before you build anything.
2 · Test object
¦ Field ¦ Sample value ¦ Where it comes from ¦
¦-------¦--------------¦---------------------¦
¦ Nominal voltage, secondary ¦ 120 V L–L (69.282 V L–N) ¦ VT 4160 : 120 ¦
¦ Nominal current, secondary ¦ 5 A ¦ CT 200 : 5 ¦
¦ VT ratio ¦ 34.667 : 1 ¦ ¦
¦ CT ratio ¦ 40 : 1 ¦ ¦
¦ Ground CT ratio ¦ 10 : 1 ¦ 50 : 5, core balance ¦
¦ Nominal frequency ¦ 60 Hz ¦ ¦
Four derived currents drive the whole plan. Write them where you can see them:
¦ Quantity ¦ Primary ¦ Secondary ¦
¦---¦---:¦---:¦
¦ Full load amps ¦ 180 A ¦ **4.500 A** ¦
¦ Service-factor amps (1.15) ¦ 207 A ¦ 5.175 A ¦
¦ Locked-rotor amps (6 × FLA) ¦ 1080 A ¦ **27.000 A** ¦
¦ 50P pickup (8 × FLA) ¦ 1440 A ¦ 36.000 A ¦
FLA secondary and locked-rotor secondary are the two the plan is written in per unit of.
The tool quotes every thermal point as a multiple of FLA and every start as a multiple of
locked rotor.
3 · Hardware configuration
**Amplifier mode: 3 × 32 A.** A motor relay has one CT set, so a second triple gains
nothing, and the 32 A limit is what the start currents need. See §7 — one element still
does not fit.
**No V 4 in this plan.** Nothing in the 869 set uses the auxiliary voltage output. Three
phase voltages and one current triple is the whole analogue picture, and the largest
voltage anywhere is 95.263 V on the 59 timing shot.
Ground current goes **through the core-balance window**, not into a phase CT. Both 50SG
and 87M depend on it, and both have pickups small enough that how the lead is routed
matters more than the setting:
¦ Element ¦ Pickup, primary ¦ Pickup, secondary ¦
¦---¦---:¦---:¦
¦ 50SG sensitive ground ¦ 0.50 A ¦ 0.050 A ¦
¦ 87M motor differential ¦ 0.200 A ¦ — ¦
Check the CMC's accuracy at those outputs before treating a marginal result as a relay
fault, and confirm the direction the conductor passes through the window: a lead routed
back the wrong way inverts the answer and looks exactly like a setting error.
Binary I/O
¦ CMC ¦ Direction ¦ To / from the relay ¦
¦-----¦-----------¦---------------------¦
¦ Bin. in 1 ¦ in ¦ Trip contact — the timing reference for every operate time ¦
¦ Bin. in 2 ¦ in ¦ Start permissive / close output — 66 blocks here, it does not trip ¦
¦ Bin. in 3 ¦ in ¦ Alarm — 49 thermal alarm at 75 % capacity ¦
¦ Bin. out 1 ¦ out ¦ 52a / contactor auxiliary ¦
¦ Bin. out 2 ¦ out ¦ 52b ¦
¦ Bin. out 3 ¦ out ¦ Breaker-failure initiate ¦
Binary input 2 is not optional. **66 does not trip — it inhibits.** A correct result is a
refused start, which is invisible on the trip contact. If the motor is allowed to start
and the relay then trips, the setting is doing the wrong thing and a trip-only test set-up
will record it as a pass.
4 · Module map
Filter `869-MTR-steps.csv` on `TU_Module`. The order below is deliberate and §5 explains
why: everything that does not disturb the thermal model comes first.
¦ Order ¦ Module ¦ Elements ¦ Steps ¦
¦------:¦--------¦----------¦------:¦
¦ 1 ¦ Voltage ¦ 27, 59 ¦ 8 ¦
¦ 2 ¦ Quick CMC ¦ 47, 81, 55, 32, 87M ¦ 17 ¦
¦ 3 ¦ Overcurrent — pickup + time ¦ 50P, 50G, 50SG, 51LR, 37 ¦ 17 ¦
¦ 4 ¦ State Sequencer ¦ 50BF (assembled from 5 steps) ¦ 5 ¦
¦ 5 ¦ Overcurrent — characteristic ¦ 46, 51G, **49** ¦ 17 ¦
¦ 6 ¦ Quick CMC ¦ **49TC** ¦ 7 ¦
¦ 7 ¦ State Sequencer ¦ 48, 66, 19 (21 sequenced states) ¦ 21 ¦
Note that the Quick CMC group is split. 49TC is a Quick CMC module like the four in row 2,
but it drives the thermal model and belongs with 49 rather than with the voltage-unbalance
and power checks. Rows 5 to 7 — the thermal characteristic, the capacity readings and the
three start sequences — are last on purpose, and §5 is why.
5 · The thermal model — plan the order or lose the day
The 49 model accumulates capacity and decays slowly. Numbers from the sample motor:
¦ Quantity ¦ Value ¦
¦---¦---¦
¦ Accumulation rate at 6 × FLA ¦ 10.01 % per second ¦
¦ Trip time at 6 × FLA, cold ¦ 9.99 s ¦
¦ Trip time at 6 × FLA, hot ¦ 7.49 s ¦
¦ Running time constant ¦ 15 min ¦
¦ Stopped time constant ¦ 30 min ¦
¦ **Full decay from 100 %** ¦ **150 min** ¦
Two and a half hours to cool from a single trip, if you wait it out. Nobody waits it out,
which is why the usual outcome is a string of short operate times that all look like the
relay is fast.
Three rules:
1. **Reset thermal capacity in the relay between every thermal point**, and record the
starting value with each result. A point taken from an unknown capacity is not a
measurement.
2. **Read capacity used off the relay's own display** during an accumulation run rather
than waiting for a trip. It is faster, and it tells you the shape of the model instead
of one point on it. That is what the 49TC steps are for.
3. **Run every thermal point in one deliberate order**, then the sequences, then stop
injecting. Going back to a thermal point after the start sequences means resetting
again.
The model is not the phase current. It runs on **Ieq = √(I1² + K·I2²)** with K = 6.0, so
an unbalanced injection trips sooner than its magnitude suggests, and the 46 unbalance
points feed the thermal model as well as the unbalance element. Expect the two to interact
and do not treat an early thermal trip during an unbalance test as a fault.
6 · The three sequences
Filter on `SeqRun` and `SeqState`. Each run is one sequence; the states go in in order.
**48 acceleration / incomplete sequence.** Start current 27.000 A at 85 % of nominal
voltage — a real start pulls the terminal voltage down, and if the relay has voltage-
dependent start supervision it will notice. Two timers race here: the acceleration timer
expires at 10.0 s and the cold thermal curve at 9.99 s. Whichever is shorter is what trips,
so record which element the relay reports, not just that it tripped.
**The sample motor deliberately fails its hot start.** The hot curve reaches trip at
7.49 s and the motor needs 8.00 s to accelerate. That is not a test-set problem and it is
not a modelling artefact — it is the finding, and it is the kind that shows up on a real
motor as "trips on the second start" months after commissioning. If your own data does
this, raise it before you tune the relay to hide it.
**66 starts per hour.** A rolling-hour counter cannot be shortcut on the test set. Either
reduce the settings for the test and restore them afterwards — recording as-found and
as-left — or accept that a full test takes an hour of wall clock. Three separate limits
can each block a start (starts per hour, time between starts, restart delay after a stop);
provoke them one at a time or you will not know which one answered.
**19 reduced-voltage start transition.** At the 65 % tap the motor draws 17.550 A, which
is 3.90 × FLA instead of 6.00 — starting current follows voltage roughly in proportion,
while torque falls with its square. The transition is set at 13.500 A. Run 2 is the one
worth doing carefully: an autotransformer tap left energised past its short-time rating is
what this element exists to catch, and a transition that simply works proves very little.
Note that at 3.90 × FLA the cold thermal curve reaches trip at 24.6 s, so check which
element the relay reports when the tap limit and the thermal model land close together.
7 · Before you inject
**50P does not fit in 3 × 32 A.** Its pickup is 8 × FLA = **36.000 A secondary**, and the
timing shot at 2 × pickup is **72.000 A**.
¦ Step ¦ Current ¦ Reachable ¦
¦---¦---:¦---¦
¦ Pickup — above threshold ¦ 37.800 A ¦ only in 1 × 64 A, single phase ¦
¦ Pickup — below threshold ¦ 34.200 A ¦ only in 1 × 64 A, single phase ¦
¦ Timing at 2.0 × pickup ¦ 72.000 A ¦ **not by a CMC 356 in any mode** ¦
Prove the pickup pair in the **1 × 64 A** arrangement, which parallels the three current
outputs into one phase, and time the element at a lower multiple — 1.5 × pickup is 54.0 A
and still reachable there. Record the multiple you actually used. Do not quietly drop the
timing test, and do not reduce the relay's pickup to make the shot fit.
While you are there: the tool flags that 50P at 36.000 A sits above the locked-rotor
current of 27.000 A, which is the right relationship. A short-circuit element set below
locked rotor trips on every start, and that is the single most common motor-relay setting
error.
**Everything else fits.** The next largest currents are 37.8 A (50P pickup, above) and
27.0 A on the start and thermal points, which the 32 A channels carry.
8 · After the first build
Save as a template with the test object detached. The module order, the binary map and the
thermal discipline carry across motors unchanged — only FLA, locked rotor and the timers
move, and those come out of the generator.
Two things this plan will not do: it will not let a thermal point taken from an unknown
starting capacity count as a measurement, and it will not record a 66 test as passed off
the trip contact, because a correct 66 never operates the trip contact at all.