## Start here
7SD82-DIF — Siemens 7SD82 SIPROTEC 5 line differential
How to use this workbook
Fill in | Only the two shaded columns on each test sheet: MEASURED and PASS / FAIL. Everything else is calculated and should not be edited by hand.
Example row | MEASURED "1.432 s", PASS / FAIL "PASS". Use the same unit the Expected column uses, so the two can be compared without conversion.
Untested steps | Record them as NOT TESTED with a reason. A blank result reads as work not yet done; it must never be left blank on a completed record.
If a setting changes | Do not edit numbers here. Change it in the relay tool, re-run the generator, and rebuild this workbook — that is what keeps the injected values and the calculations from drifting apart.
Where these values come from
Plan | 7SD82-DIF — Siemens 7SD82 SIPROTEC 5 line differential
Generated | generated 2026-09-05 12:28 from 7SD82.html
Configuration | kv=110; freq=50; len=15; type=cable; iref=600; ich=25; ctAp=600; ctAs=1; ctAstar=line; ctBp=600; ctBs=1; ctBstar=line; stage=local; vtp=110000; vts=100; vtc=wye; comm=fibre; tprop=0.5; tasym=0.2; sync=pp; cmc=6x; imax=12.5; vmax=300
Conventions | All quantities are SECONDARY at the relay terminals. Angles in degrees, CCW positive, V L1 = 0.
Sample data | Values shown are for the tool's sample configuration — re-generate after entering real station data.
Staging | Staging is local. Steps marked "both ends" in CurrentNeededAt need current at the remote end; at local-end staging they cannot be run and must be recorded as untested, not as passed.
Record identification
Station
Feeder / plant item
Device serial
Firmware
Setting file revision
Test set serial
Tested by
Date
Witnessed by
Sheets in this workbook
Test steps | 69 test steps — the record. Fill in MEASURED and PASS / FAIL.
Channels | 407 rows — one per channel per step, for pasting into a Test Universe module table.
Test steps (loopback) | 69 test steps — the record. Fill in MEASURED and PASS / FAIL.
Channels (loopback) | 407 rows — one per channel per step, for pasting into a Test Universe module table.
Build guide | How to assemble this plan in Test Universe, and the thing about this relay most likely to be got wrong.
Progress
Total steps
Results entered
Passed
Failed
Not tested
Outstanding
Counts refer to the first test sheet only.

## Test steps
Function | Description | TU module | Drive as | # | Test step | What is applied | Run | State | Dur s | V L1 | V L2 | V L3 | V 4 | I L1 | I L2 | I L3 | I B-L1 | I B-L2 | I B-L3 | Hz | Current at | Reachable | Expected | Expected — detail | MEASURED | PASS / FAIL
87L | Line differential | Differential | characteristic | 1 | Minimum pickup — above | End A alone at 0.345 pu, end B quiescent. The whole injected current is differential. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3450@0.0 | 0.3450@-120.0 | 0.3450@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 2 | Minimum pickup — below | End A alone at 0.255 pu, end B quiescent. The whole injected current is differential. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.2550@0.0 | 0.2550@-120.0 | 0.2550@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above | Required Idiff 0.300 pu, applied 0.345 pu. End A 0.672 pu, end B 0.328 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.6725@0.0 | 0.6725@-120.0 | 0.6725@120.0 | 0.3275@180.0 | 0.3275@60.0 | 0.3275@-60.0 | 50 | both ends | NO — staging is local end only | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below | Required Idiff 0.300 pu, applied 0.255 pu. End A 0.627 pu, end B 0.372 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.6275@0.0 | 0.6275@-120.0 | 0.6275@120.0 | 0.3725@180.0 | 0.3725@60.0 | 0.3725@-60.0 | 50 | both ends | NO — staging is local end only | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above | Required Idiff 0.900 pu, applied 1.035 pu. End A 2.018 pu, end B 0.983 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.0175@0.0 | 2.0175@-120.0 | 2.0175@120.0 | 0.9825@180.0 | 0.9825@60.0 | 0.9825@-60.0 | 50 | both ends | NO — staging is local end only | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below | Required Idiff 0.900 pu, applied 0.765 pu. End A 1.882 pu, end B 1.118 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.8825@0.0 | 1.8825@-120.0 | 1.8825@120.0 | 1.1175@180.0 | 1.1175@60.0 | 1.1175@-60.0 | 50 | both ends | NO — staging is local end only | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above | Required Idiff 3.200 pu, applied 3.680 pu. End A 5.840 pu, end B 2.160 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 5.8400@0.0 | 5.8400@-120.0 | 5.8400@120.0 | 2.1600@180.0 | 2.1600@60.0 | 2.1600@-60.0 | 50 | both ends | NO — staging is local end only | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below | Required Idiff 3.200 pu, applied 2.720 pu. End A 5.360 pu, end B 2.640 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 5.3600@0.0 | 5.3600@-120.0 | 5.3600@120.0 | 2.6400@180.0 | 2.6400@60.0 | 2.6400@-60.0 | 50 | both ends | NO — staging is local end only | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 9 | Through-current stability | Both ends matched and opposed at 8.0 pu — an external fault. This is the polarity and ratio test. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 8.0000@0.0 | 8.0000@-120.0 | 8.0000@120.0 | 8.0000@180.0 | 8.0000@60.0 | 8.0000@-60.0 | 50 | both ends | NO — staging is local end only | RESTRAIN | Zero differential; any standing value is a wiring or ratio error
87L | Line differential | Differential | characteristic | 10 | Internal fault | Both ends feeding into the line at 4.0 pu — the condition the scheme exists for. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 4.0000@0.0 | 4.0000@-120.0 | 4.0000@120.0 | 4.0000@0.0 | 4.0000@-120.0 | 4.0000@120.0 | 50 | both ends | NO — staging is local end only | OPERATE | Idiff equals the sum of both infeeds
87N | Ground differential | Quick CMC | points | 1 | Threshold — above | Single-phase into end A at 0.115 pu, giving 3I0 equal to it. End B quiescent. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.1150@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | OPERATE | Operate within 50.0 ms
87N | Ground differential | Quick CMC | points | 2 | Threshold — below | Single-phase into end A at 0.085 pu, giving 3I0 equal to it. End B quiescent. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0850@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | RESTRAIN | No operation
87N | Ground differential | Quick CMC | points | 3 | Through-current stability | Both ends matched and opposed at 4.0 pu residual |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 4.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 4.0000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | both ends | NO — staging is local end only | RESTRAIN | Zero residual differential
Ich | Charging current compensation | Quick CMC | points | 1 | Standing differential at nominal voltage | Both ends carrying rated load opposed, but end B short by the charging current — which is what a healthy energised line actually looks like. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@0.0 | 1.0000@-120.0 | 1.0000@120.0 | 0.9583@180.0 | 0.9583@60.0 | 0.9583@-60.0 | 50 | both ends | NO — staging is local end only | NO ALARM | Compensation should reduce it to under 0.0083 pu
Ich | Charging current compensation | Quick CMC | points | 2 | Over-compensation check | Charging current doubled — the value entered in the device is now half what the line is really drawing. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@0.0 | 1.0000@-120.0 | 1.0000@120.0 | 0.9167@180.0 | 0.9167@60.0 | 0.9167@-60.0 | 50 | both ends | NO — staging is local end only | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself
Ich | Charging current compensation | Quick CMC | points | 3 | True through current | Both ends exactly matched — no charging current at all, which is what a de-energised line under injection looks like. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@0.0 | 1.0000@-120.0 | 1.0000@120.0 | 1.0000@180.0 | 1.0000@60.0 | 1.0000@-60.0 | 50 | both ends | NO — staging is local end only | NO DIFFERENTIAL | This is the reference the other two points are measured against
PI | Protection interface and synchronisation | — | link / no injection | 1 | Measured delay | Read the delay the device reports and compare with 0.50 ms | [15 empty] | yes | WITHIN TOLERANCE | A reading far from the expected value means the route is not the one on the drawing
PI | Protection interface and synchronisation | — | link / no injection | 2 | Asymmetry | Read the reported send/receive difference | [15 empty] | yes | UNDER 0.20 ms | Ping-pong synchronisation assumes a symmetric path — asymmetry appears directly as a phase error between the ends
PI | Protection interface and synchronisation | — | link / no injection | 3 | Link interrupted | Disconnect the fibre or disable the channel and hold for longer than 0.100 s | [15 empty] | yes | 87L BLOCKS, BACKUP ARMS | Confirm the backup functions actually take over, not just that the differential drops out
PI | Protection interface and synchronisation | — | link / no injection | 4 | Link restored | Reconnect and wait for the interface to resynchronise | [15 empty] | yes | 87L RETURNS | Note the resynchronisation time — it is dead time on the protection
PI | Protection interface and synchronisation | — | link / no injection | 5 | Injection during outage | With the link down, apply an internal-fault current at end A | [15 empty] | yes | BACKUP CLEARS IT | This is the point that proves the fallback is real rather than nominal
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 1 | A to B, each signal | Assert each configured bit at end A in turn and confirm the matching output at end B | [15 empty] | yes | RECEIVED | One at a time — a swapped pair passes a both-at-once test
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 2 | B to A, each signal | The same in the other direction | [15 empty] | yes | RECEIVED | Both directions are separately configurable and separately wrong
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 3 | Transfer time | Time from assertion at one end to output at the other | [15 empty] | yes | ABOUT 15 ms | Against a link delay of 0.50 ms one way — the difference is device processing
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 4 | Link down | Assert a signal with the interface disconnected | [15 empty] | yes | NOT RECEIVED, ALARM | The receiving end must not hold the last state as though it were live
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 5 | Direct transfer trip | Assert the DTT bit and confirm it trips the remote breaker | [15 empty] | yes | REMOTE TRIP | The one signal that operates plant directly — worth proving on its own, not as part of a batch
50-1 | Backup overcurrent stage 1 | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.1000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate within 0.300 s
50-1 | Backup overcurrent stage 1 | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.9000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
50-1 | Backup overcurrent stage 1 | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 4.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.300 s | Measured from the current step to the trip
51 | Backup overcurrent inverse | Overcurrent | characteristic | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.2600@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Long operate time — let the characteristic run out
51 | Backup overcurrent inverse | Overcurrent | characteristic | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.1400@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
51 | Backup overcurrent inverse | Overcurrent | characteristic | 3 | Timing at 2.0× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 2.006 s | From the characteristic equation
51 | Backup overcurrent inverse | Overcurrent | characteristic | 4 | Timing at 3.0× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 3.6000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 1.260 s | From the characteristic equation
51 | Backup overcurrent inverse | Overcurrent | characteristic | 5 | Timing at 5.0× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 6.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.856 s | From the characteristic equation
50N-1 | Backup ground overcurrent | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.4200@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate within 0.300 s
50N-1 | Backup ground overcurrent | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3800@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
50N-1 | Backup ground overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.8000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.300 s | Measured from the current step to the trip
Stub | Stub bus protection | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive | Line isolator auxiliary contact indicating closed, current well above the stub threshold |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO STUB TRIP | 87L is in service and owns this current instead
Stub | Stub bus protection | Overcurrent | pickup+time | 2 | Isolator open — above threshold | Isolator auxiliary indicating open, so the stub function is armed |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0500@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | TRIP | Operate within 50.0 ms
Stub | Stub bus protection | Overcurrent | pickup+time | 3 | Isolator open — below threshold | 95% of the stub threshold |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.9500@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO TRIP | No operation
Stub | Stub bus protection | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out | Current at end A only with the isolator open — the differential would see this as an internal fault if it were still in service |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated
79 | Auto-reclose | State Sequencer | sequence | 1 | Prefault load | Healthy line, scheme ready | 1 | 1/3 | 2 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@-75.0 | 1.0000@165.0 | 1.0000@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | READY | Cycle counter at zero
79 | Auto-reclose | State Sequencer | sequence | 2 | Fault 1 of 1 | Internal fault at end A, 4.0 × In | 1 | 2/3 | 0.03 | 17.321@0.0 | 17.321@-120.0 | 17.321@120.0 |  | 4.0000@-75.0 | 4.0000@165.0 | 4.0000@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end
79 | Auto-reclose | State Sequencer | sequence | 3 | Final trip | No cycles left | 1 | 3/3 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | FINAL TRIP | Scheme blocked until reset
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above | 105% of the detector, no initiate |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.1050@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | DETECTOR PICKED UP | Flag only
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below | 95% of the detector |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0950@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO PICKUP | Must drop out
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | Initiate asserted, current held |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.150 s | Stage 1
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing | Same state, second stage |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.250 s | Stage 2
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | Initiate asserted, then current removed inside stage 1 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO TRIP | Detector reset stops the scheme
74TC | Trip circuit supervision | — | binary / DC | 1 | Healthy circuit | Trip circuit intact, breaker closed | [15 empty] | yes | NO ALARM | Both inputs energised
74TC | Trip circuit supervision | — | binary / DC | 2 | Trip coil open | Open the coil circuit at the terminal block | [15 empty] | yes | ALARM | After 2.000 s
74TC | Trip circuit supervision | — | binary / DC | 3 | Trip supply lost | Remove the DC supply | [15 empty] | yes | ALARM | After 2.000 s
74TC | Trip circuit supervision | — | binary / DC | 4 | Breaker open | Breaker open with the circuit intact | [15 empty] | yes | NO ALARM | The point that catches a one-input arrangement wired as if it were two
25 | Synchrocheck | Synchronizer | points | 1 | In synchronism | All differences well inside their limits |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz
25 | Synchrocheck | Synchronizer | points | 2 | Angle inside limit | Angle at 80% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@9.6 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | CLOSE RELEASED | Δθ 9.6°
25 | Synchrocheck | Synchronizer | points | 3 | Angle outside limit | Angle at 120% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@14.4 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | BLOCKED | Δθ 14.4°
25 | Synchrocheck | Synchronizer | points | 4 | Voltage difference outside | Angle matched, magnitude offset past ΔV |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 50.535@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | BLOCKED | ΔV 7.20 V
25 | Synchrocheck | Synchronizer | points | 5 | Slip outside limit | Line output off frequency so the angle rotates |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | BLOCKED | Δf 0.060 Hz
25 | Synchrocheck | Synchronizer | points | 6 | Dead line, live bus | Line collapsed below the dead threshold |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | CLOSE RELEASED | From the dead-line logic
27 | Undervoltage | Voltage | pickup+time | 1 | Threshold — below | 95% of setting |  |  |  | 43.879@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate after 2.000 s
27 | Undervoltage | Voltage | pickup+time | 2 | Threshold — above | 105% of setting |  |  |  | 48.497@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
27 | Undervoltage | Voltage | pickup+time | 3 | Timing at 0.50× threshold | Step from nominal |  |  |  | 23.094@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 2.000 s | Definite time
59 | Overvoltage | Voltage | pickup+time | 1 | Threshold — above | 105% of setting |  |  |  | 69.715@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate after 2.000 s
59 | Overvoltage | Voltage | pickup+time | 2 | Threshold — below | 95% of setting |  |  |  | 63.076@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
59 | Overvoltage | Voltage | pickup+time | 3 | Timing at 1.30× threshold | Step from nominal |  |  |  | 86.314@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 2.000 s | Definite time
81 | Under / over frequency | Quick CMC | points | 1 | Threshold — past | 0.050 Hz beyond the setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 48.95 |  | yes | OPERATE | Operate after 0.500 s
81 | Under / over frequency | Quick CMC | points | 2 | Threshold — short of | 0.050 Hz on the healthy side |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 49.05 |  | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 3 | Timing | Step from 50.0 Hz |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 48.95 |  | yes | 0.500 s | Definite time
81 | Under / over frequency | Quick CMC | points | 4 | Below minimum voltage | Voltage under the 30 V level |  |  |  | 24.000@0.0 | 24.000@-120.0 | 24.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 48.95 |  | yes | BLOCKED | Function inhibited

## Channels
Function | Description | Group | TU module | Drive as | # | Test step | Run | State | State label | Dur s | Channel | Magnitude | Unit | Angle deg | Hz | Note | Expected | Expected — detail | Verdict | Current at
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I A-L1 | 0.345 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I A-L2 | 0.345 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I A-L3 | 0.345 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I A-L1 | 0.255 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I A-L2 | 0.255 | A | -120 | 50 | end A | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I A-L3 | 0.255 | A | 120 | 50 | end A | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I A-L1 | 0.6725 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I A-L2 | 0.6725 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I A-L3 | 0.6725 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I B-L1 | 0.3275 | A | 180 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I B-L2 | 0.3275 | A | 60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I B-L3 | 0.3275 | A | -60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I A-L1 | 0.6275 | A | 0 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I A-L2 | 0.6275 | A | -120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I A-L3 | 0.6275 | A | 120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I B-L1 | 0.3725 | A | 180 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I B-L2 | 0.3725 | A | 60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I B-L3 | 0.3725 | A | -60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I A-L1 | 2.0175 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I A-L2 | 2.0175 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I A-L3 | 2.0175 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I B-L1 | 0.9825 | A | 180 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I B-L2 | 0.9825 | A | 60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I B-L3 | 0.9825 | A | -60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I A-L1 | 1.8825 | A | 0 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I A-L2 | 1.8825 | A | -120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I A-L3 | 1.8825 | A | 120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I B-L1 | 1.1175 | A | 180 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I B-L2 | 1.1175 | A | 60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I B-L3 | 1.1175 | A | -60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I A-L1 | 5.84 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I A-L2 | 5.84 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I A-L3 | 5.84 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I B-L1 | 2.16 | A | 180 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I B-L2 | 2.16 | A | 60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I B-L3 | 2.16 | A | -60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I A-L1 | 5.36 | A | 0 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I A-L2 | 5.36 | A | -120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I A-L3 | 5.36 | A | 120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I B-L1 | 2.64 | A | 180 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I B-L2 | 2.64 | A | 60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I B-L3 | 2.64 | A | -60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I A-L1 | 8 | A | 0 | 50 | end A | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I A-L2 | 8 | A | -120 | 50 | end A | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I A-L3 | 8 | A | 120 | 50 | end A | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I B-L1 | 8 | A | 180 | 50 | end B | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I B-L2 | 8 | A | 60 | 50 | end B | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I B-L3 | 8 | A | -60 | 50 | end B | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I A-L1 | 4 | A | 0 | 50 | end A | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I A-L2 | 4 | A | -120 | 50 | end A | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I A-L3 | 4 | A | 120 | 50 | end A | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I B-L1 | 4 | A | 0 | 50 | end B | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I B-L2 | 4 | A | -120 | 50 | end B | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I B-L3 | 4 | A | 120 | 50 | end B | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I A-L1 | 0.115 | A | 0 | 50 | end A | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I A-L1 | 0.085 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I A-L1 | 4 | A | 0 | 50 | end A | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I B-L1 | 4 | A | 180 | 50 | end B | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | RESTRAIN | Zero residual differential | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I A-L1 | 1 | A | 0 | 50 | end A | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I A-L2 | 1 | A | -120 | 50 | end A | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I A-L3 | 1 | A | 120 | 50 | end A | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I B-L1 | 0.9583 | A | 180 | 50 | end B | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I B-L2 | 0.9583 | A | 60 | 50 | end B | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I B-L3 | 0.9583 | A | -60 | 50 | end B | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I A-L1 | 1 | A | 0 | 50 | end A | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I A-L2 | 1 | A | -120 | 50 | end A | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I A-L3 | 1 | A | 120 | 50 | end A | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I B-L1 | 0.9167 | A | 180 | 50 | end B | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I B-L2 | 0.9167 | A | 60 | 50 | end B | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I B-L3 | 0.9167 | A | -60 | 50 | end B | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I A-L1 | 1 | A | 0 | 50 | end A | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I A-L2 | 1 | A | -120 | 50 | end A | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I A-L3 | 1 | A | 120 | 50 | end A | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I B-L1 | 1 | A | 180 | 50 | end B | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I B-L2 | 1 | A | 60 | 50 | end B | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I B-L3 | 1 | A | -60 | 50 | end B | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
PI | Protection interface and synchronisation | Differential | — | link / no injection | 1 | Measured delay |  |  |  |  | (no injection) |  |  |  |  | Read the delay the device reports and compare with 0.50 ms | WITHIN TOLERANCE | A reading far from the expected value means the route is not the one on the drawing | nu
PI | Protection interface and synchronisation | Differential | — | link / no injection | 2 | Asymmetry |  |  |  |  | (no injection) |  |  |  |  | Read the reported send/receive difference | UNDER 0.20 ms | Ping-pong synchronisation assumes a symmetric path — asymmetry appears directly as a phase error between the ends | nu
PI | Protection interface and synchronisation | Differential | — | link / no injection | 3 | Link interrupted |  |  |  |  | (no injection) |  |  |  |  | Disconnect the fibre or disable the channel and hold for longer than 0.100 s | 87L BLOCKS, BACKUP ARMS | Confirm the backup functions actually take over, not just that the differential drops out | op
PI | Protection interface and synchronisation | Differential | — | link / no injection | 4 | Link restored |  |  |  |  | (no injection) |  |  |  |  | Reconnect and wait for the interface to resynchronise | 87L RETURNS | Note the resynchronisation time — it is dead time on the protection | op
PI | Protection interface and synchronisation | Differential | — | link / no injection | 5 | Injection during outage |  |  |  |  | (no injection) |  |  |  |  | With the link down, apply an internal-fault current at end A | BACKUP CLEARS IT | This is the point that proves the fallback is real rather than nominal | op
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 1 | A to B, each signal |  |  |  |  | (no injection) |  |  |  |  | Assert each configured bit at end A in turn and confirm the matching output at end B | RECEIVED | One at a time — a swapped pair passes a both-at-once test | op
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 2 | B to A, each signal |  |  |  |  | (no injection) |  |  |  |  | The same in the other direction | RECEIVED | Both directions are separately configurable and separately wrong | op
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 3 | Transfer time |  |  |  |  | (no injection) |  |  |  |  | Time from assertion at one end to output at the other | ABOUT 15 ms | Against a link delay of 0.50 ms one way — the difference is device processing | nu
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 4 | Link down |  |  |  |  | (no injection) |  |  |  |  | Assert a signal with the interface disconnected | NOT RECEIVED, ALARM | The receiving end must not hold the last state as though it were live | no
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 5 | Direct transfer trip |  |  |  |  | (no injection) |  |  |  |  | Assert the DTT bit and confirm it trips the remote breaker | REMOTE TRIP | The one signal that operates plant directly — worth proving on its own, not as part of a batch | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L1 | 2.1 | A | -75 | 50 | end A | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L1 | 1.9 | A | -75 | 50 | end A | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L1 | 4 | A | -75 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I A-L1 | 1.26 | A | -75 | 50 | end A | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I A-L1 | 1.14 | A | -75 | 50 | end A | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L1 | 2.4 | A | -75 | 50 | end A | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | I A-L1 | 3.6 | A | -75 | 50 | end A | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | I A-L1 | 6 | A | -75 | 50 | end A | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.856 s | From the characteristic equation | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L1 | 0.42 | A | -75 | 50 | end A | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L1 | 0.38 | A | -75 | 50 | end A | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L1 | 0.8 | A | -75 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | I A-L1 | 2 | A | -75 | 50 | end A | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | I A-L1 | 1.05 | A | -75 | 50 | end A | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | I A-L1 | 0.95 | A | -75 | 50 | end A | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | I A-L1 | 2 | A | -75 | 50 | end A | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | V L1 | 57.735 | V | 0 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | V L2 | 57.735 | V | -120 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | V L3 | 57.735 | V | 120 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I A-L1 | 1 | A | -75 | 50 | end A | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I A-L2 | 1 | A | 165 | 50 | end A | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I A-L3 | 1 | A | 45 | 50 | end A | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I B-L1 | 0 | A | 0 | 50 | end B | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I B-L2 | 0 | A | 0 | 50 | end B | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I B-L3 | 0 | A | 0 | 50 | end B | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | V L1 | 17.321 | V | 0 | 50 |  | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | V L2 | 17.321 | V | -120 | 50 |  | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | V L3 | 17.321 | V | 120 | 50 |  | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I A-L1 | 4 | A | -75 | 50 | end A | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I A-L2 | 4 | A | 165 | 50 | end A | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I A-L3 | 4 | A | 45 | 50 | end A | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I B-L1 | 0 | A | 0 | 50 | end B | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I B-L2 | 0 | A | 0 | 50 | end B | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I B-L3 | 0 | A | 0 | 50 | end B | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | V L1 | 0 | V | 0 | 50 |  | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | V L2 | 0 | V | -120 | 50 |  | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | V L3 | 0 | V | 120 | 50 |  | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I A-L1 | 0 | A | 0 | 50 | end A | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I A-L2 | 0 | A | 0 | 50 | end A | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I A-L3 | 0 | A | 0 | 50 | end A | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I B-L1 | 0 | A | 0 | 50 | end B | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I B-L2 | 0 | A | 0 | 50 | end B | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I B-L3 | 0 | A | 0 | 50 | end B | FINAL TRIP | Scheme blocked until reset | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I A-L1 | 0.105 | A | -75 | 50 | end A | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I A-L1 | 0.095 | A | -75 | 50 | end A | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I A-L1 | 0.3 | A | -75 | 50 | end A | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I A-L1 | 0.3 | A | -75 | 50 | end A | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I A-L1 | 0 | A | -75 | 50 | end A | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO TRIP | Detector reset stops the scheme | no
74TC | Trip circuit supervision | Automation | — | binary / DC | 1 | Healthy circuit |  |  |  |  | (no injection) |  |  |  |  | Trip circuit intact, breaker closed | NO ALARM | Both inputs energised | no
74TC | Trip circuit supervision | Automation | — | binary / DC | 2 | Trip coil open |  |  |  |  | (no injection) |  |  |  |  | Open the coil circuit at the terminal block | ALARM | After 2.000 s | op
74TC | Trip circuit supervision | Automation | — | binary / DC | 3 | Trip supply lost |  |  |  |  | (no injection) |  |  |  |  | Remove the DC supply | ALARM | After 2.000 s | op
74TC | Trip circuit supervision | Automation | — | binary / DC | 4 | Breaker open |  |  |  |  | (no injection) |  |  |  |  | Breaker open with the circuit intact | NO ALARM | The point that catches a one-input arrangement wired as if it were two | no
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V 4 | 57.735 | V | 0 | 50 | line side | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V 4 | 57.735 | V | 9.6 | 50 | line side | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V 4 | 57.735 | V | 14.4 | 50 | line side | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V 4 | 50.535 | V | 0 | 50 | line side | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V 4 | 57.735 | V | 0 | 50.06 | line side — 50.060 Hz | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V 4 | 10 | V | 0 | 50 | line side | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | From the dead-line logic | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L1 | 43.879 | V | 0 | 50 | depressed phase | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L1 | 48.497 | V | 0 | 50 | depressed phase | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | V L1 | 23.094 | V | 0 | 50 | depressed phase | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 69.715 | V | 0 | 50 | raised phase | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 63.076 | V | 0 | 50 | raised phase | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | V L1 | 86.314 | V | 0 | 50 | raised phase | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L1 | 57.735 | V | 0 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L2 | 57.735 | V | -120 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L3 | 57.735 | V | 120 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I A-L1 | 0 | A | 0 | 48.95 | end A | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I A-L2 | 0 | A | 0 | 48.95 | end A | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I A-L3 | 0 | A | 0 | 48.95 | end A | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L1 | 57.735 | V | 0 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L2 | 57.735 | V | -120 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L3 | 57.735 | V | 120 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I A-L1 | 0 | A | 0 | 49.05 | end A | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I A-L2 | 0 | A | 0 | 49.05 | end A | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I A-L3 | 0 | A | 0 | 49.05 | end A | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L1 | 57.735 | V | 0 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L2 | 57.735 | V | -120 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L3 | 57.735 | V | 120 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I A-L1 | 0 | A | 0 | 48.95 | end A | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I A-L2 | 0 | A | 0 | 48.95 | end A | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I A-L3 | 0 | A | 0 | 48.95 | end A | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L1 | 24 | V | 0 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L2 | 24 | V | -120 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L3 | 24 | V | 120 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I A-L1 | 0 | A | 0 | 48.95 | end A | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I A-L2 | 0 | A | 0 | 48.95 | end A | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I A-L3 | 0 | A | 0 | 48.95 | end A | BLOCKED | Function inhibited | no

## Test steps (loopback)
Function | Description | TU module | Drive as | # | Test step | What is applied | Run | State | Dur s | V L1 | V L2 | V L3 | V 4 | I L1 | I L2 | I L3 | I B-L1 | I B-L2 | I B-L3 | Hz | Current at | Reachable | Expected | Expected — detail | MEASURED | PASS / FAIL
87L | Line differential | Differential | characteristic | 1 | Minimum pickup — above | End A alone at 0.345 pu, end B quiescent. The whole injected current is differential. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3450@0.0 | 0.3450@-120.0 | 0.3450@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 2 | Minimum pickup — below | End A alone at 0.255 pu, end B quiescent. The whole injected current is differential. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.2550@0.0 | 0.2550@-120.0 | 0.2550@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above | Required Idiff 0.300 pu, applied 0.345 pu. End A 0.672 pu, end B 0.328 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.6725@0.0 | 0.6725@-120.0 | 0.6725@120.0 | 0.3275@180.0 | 0.3275@60.0 | 0.3275@-60.0 | 50 | both ends | yes | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below | Required Idiff 0.300 pu, applied 0.255 pu. End A 0.627 pu, end B 0.372 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.6275@0.0 | 0.6275@-120.0 | 0.6275@120.0 | 0.3725@180.0 | 0.3725@60.0 | 0.3725@-60.0 | 50 | both ends | yes | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above | Required Idiff 0.900 pu, applied 1.035 pu. End A 2.018 pu, end B 0.983 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.0175@0.0 | 2.0175@-120.0 | 2.0175@120.0 | 0.9825@180.0 | 0.9825@60.0 | 0.9825@-60.0 | 50 | both ends | yes | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below | Required Idiff 0.900 pu, applied 0.765 pu. End A 1.882 pu, end B 1.118 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.8825@0.0 | 1.8825@-120.0 | 1.8825@120.0 | 1.1175@180.0 | 1.1175@60.0 | 1.1175@-60.0 | 50 | both ends | yes | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above | Required Idiff 3.200 pu, applied 3.680 pu. End A 5.840 pu, end B 2.160 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 5.8400@0.0 | 5.8400@-120.0 | 5.8400@120.0 | 2.1600@180.0 | 2.1600@60.0 | 2.1600@-60.0 | 50 | both ends | yes | OPERATE | Operate — no intentional delay
87L | Line differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below | Required Idiff 3.200 pu, applied 2.720 pu. End A 5.360 pu, end B 2.640 pu opposed. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 5.3600@0.0 | 5.3600@-120.0 | 5.3600@120.0 | 2.6400@180.0 | 2.6400@60.0 | 2.6400@-60.0 | 50 | both ends | yes | RESTRAIN | No operation
87L | Line differential | Differential | characteristic | 9 | Through-current stability | Both ends matched and opposed at 8.0 pu — an external fault. This is the polarity and ratio test. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 8.0000@0.0 | 8.0000@-120.0 | 8.0000@120.0 | 8.0000@180.0 | 8.0000@60.0 | 8.0000@-60.0 | 50 | both ends | yes | RESTRAIN | Zero differential; any standing value is a wiring or ratio error
87L | Line differential | Differential | characteristic | 10 | Internal fault | Both ends feeding into the line at 4.0 pu — the condition the scheme exists for. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 4.0000@0.0 | 4.0000@-120.0 | 4.0000@120.0 | 4.0000@0.0 | 4.0000@-120.0 | 4.0000@120.0 | 50 | both ends | yes | OPERATE | Idiff equals the sum of both infeeds
87N | Ground differential | Quick CMC | points | 1 | Threshold — above | Single-phase into end A at 0.115 pu, giving 3I0 equal to it. End B quiescent. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.1150@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | OPERATE | Operate within 50.0 ms
87N | Ground differential | Quick CMC | points | 2 | Threshold — below | Single-phase into end A at 0.085 pu, giving 3I0 equal to it. End B quiescent. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0850@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | RESTRAIN | No operation
87N | Ground differential | Quick CMC | points | 3 | Through-current stability | Both ends matched and opposed at 4.0 pu residual |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 4.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 4.0000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | both ends | yes | RESTRAIN | Zero residual differential
Ich | Charging current compensation | Quick CMC | points | 1 | Standing differential at nominal voltage | Both ends carrying rated load opposed, but end B short by the charging current — which is what a healthy energised line actually looks like. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@0.0 | 1.0000@-120.0 | 1.0000@120.0 | 0.9583@180.0 | 0.9583@60.0 | 0.9583@-60.0 | 50 | both ends | yes | NO ALARM | Compensation should reduce it to under 0.0083 pu
Ich | Charging current compensation | Quick CMC | points | 2 | Over-compensation check | Charging current doubled — the value entered in the device is now half what the line is really drawing. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@0.0 | 1.0000@-120.0 | 1.0000@120.0 | 0.9167@180.0 | 0.9167@60.0 | 0.9167@-60.0 | 50 | both ends | yes | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself
Ich | Charging current compensation | Quick CMC | points | 3 | True through current | Both ends exactly matched — no charging current at all, which is what a de-energised line under injection looks like. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@0.0 | 1.0000@-120.0 | 1.0000@120.0 | 1.0000@180.0 | 1.0000@60.0 | 1.0000@-60.0 | 50 | both ends | yes | NO DIFFERENTIAL | This is the reference the other two points are measured against
PI | Protection interface and synchronisation | — | link / no injection | 1 | Measured delay | Read the delay the device reports and compare with 0.50 ms | [15 empty] | yes | WITHIN TOLERANCE | A reading far from the expected value means the route is not the one on the drawing
PI | Protection interface and synchronisation | — | link / no injection | 2 | Asymmetry | Read the reported send/receive difference | [15 empty] | yes | UNDER 0.20 ms | Ping-pong synchronisation assumes a symmetric path — asymmetry appears directly as a phase error between the ends
PI | Protection interface and synchronisation | — | link / no injection | 3 | Link interrupted | Disconnect the fibre or disable the channel and hold for longer than 0.100 s | [15 empty] | yes | 87L BLOCKS, BACKUP ARMS | Confirm the backup functions actually take over, not just that the differential drops out
PI | Protection interface and synchronisation | — | link / no injection | 4 | Link restored | Reconnect and wait for the interface to resynchronise | [15 empty] | yes | 87L RETURNS | Note the resynchronisation time — it is dead time on the protection
PI | Protection interface and synchronisation | — | link / no injection | 5 | Injection during outage | With the link down, apply an internal-fault current at end A | [15 empty] | yes | BACKUP CLEARS IT | This is the point that proves the fallback is real rather than nominal
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 1 | A to B, each signal | Assert each configured bit at end A in turn and confirm the matching output at end B | [15 empty] | yes | RECEIVED | One at a time — a swapped pair passes a both-at-once test
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 2 | B to A, each signal | The same in the other direction | [15 empty] | yes | RECEIVED | Both directions are separately configurable and separately wrong
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 3 | Transfer time | Time from assertion at one end to output at the other | [15 empty] | yes | ABOUT 15 ms | Against a link delay of 0.50 ms one way — the difference is device processing
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 4 | Link down | Assert a signal with the interface disconnected | [15 empty] | yes | NOT RECEIVED, ALARM | The receiving end must not hold the last state as though it were live
85 | Intertrip over the interface | State Sequencer | sequence (assemble from these steps) | 5 | Direct transfer trip | Assert the DTT bit and confirm it trips the remote breaker | [15 empty] | yes | REMOTE TRIP | The one signal that operates plant directly — worth proving on its own, not as part of a batch
50-1 | Backup overcurrent stage 1 | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.1000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate within 0.300 s
50-1 | Backup overcurrent stage 1 | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.9000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
50-1 | Backup overcurrent stage 1 | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 4.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.300 s | Measured from the current step to the trip
51 | Backup overcurrent inverse | Overcurrent | characteristic | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.2600@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Long operate time — let the characteristic run out
51 | Backup overcurrent inverse | Overcurrent | characteristic | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.1400@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
51 | Backup overcurrent inverse | Overcurrent | characteristic | 3 | Timing at 2.0× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 2.006 s | From the characteristic equation
51 | Backup overcurrent inverse | Overcurrent | characteristic | 4 | Timing at 3.0× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 3.6000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 1.260 s | From the characteristic equation
51 | Backup overcurrent inverse | Overcurrent | characteristic | 5 | Timing at 5.0× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 6.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.856 s | From the characteristic equation
50N-1 | Backup ground overcurrent | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.4200@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate within 0.300 s
50N-1 | Backup ground overcurrent | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3800@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
50N-1 | Backup ground overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.8000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.300 s | Measured from the current step to the trip
Stub | Stub bus protection | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive | Line isolator auxiliary contact indicating closed, current well above the stub threshold |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO STUB TRIP | 87L is in service and owns this current instead
Stub | Stub bus protection | Overcurrent | pickup+time | 2 | Isolator open — above threshold | Isolator auxiliary indicating open, so the stub function is armed |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0500@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | TRIP | Operate within 50.0 ms
Stub | Stub bus protection | Overcurrent | pickup+time | 3 | Isolator open — below threshold | 95% of the stub threshold |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.9500@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO TRIP | No operation
Stub | Stub bus protection | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out | Current at end A only with the isolator open — the differential would see this as an internal fault if it were still in service |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated
79 | Auto-reclose | State Sequencer | sequence | 1 | Prefault load | Healthy line, scheme ready | 1 | 1/3 | 2 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@-75.0 | 1.0000@165.0 | 1.0000@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | READY | Cycle counter at zero
79 | Auto-reclose | State Sequencer | sequence | 2 | Fault 1 of 1 | Internal fault at end A, 4.0 × In | 1 | 2/3 | 0.03 | 17.321@0.0 | 17.321@-120.0 | 17.321@120.0 |  | 4.0000@-75.0 | 4.0000@165.0 | 4.0000@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end
79 | Auto-reclose | State Sequencer | sequence | 3 | Final trip | No cycles left | 1 | 3/3 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 |  | yes | FINAL TRIP | Scheme blocked until reset
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above | 105% of the detector, no initiate |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.1050@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | DETECTOR PICKED UP | Flag only
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below | 95% of the detector |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0950@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO PICKUP | Must drop out
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | Initiate asserted, current held |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.150 s | Stage 1
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing | Same state, second stage |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 0.250 s | Stage 2
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | Initiate asserted, then current removed inside stage 1 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | NO TRIP | Detector reset stops the scheme
74TC | Trip circuit supervision | — | binary / DC | 1 | Healthy circuit | Trip circuit intact, breaker closed | [15 empty] | yes | NO ALARM | Both inputs energised
74TC | Trip circuit supervision | — | binary / DC | 2 | Trip coil open | Open the coil circuit at the terminal block | [15 empty] | yes | ALARM | After 2.000 s
74TC | Trip circuit supervision | — | binary / DC | 3 | Trip supply lost | Remove the DC supply | [15 empty] | yes | ALARM | After 2.000 s
74TC | Trip circuit supervision | — | binary / DC | 4 | Breaker open | Breaker open with the circuit intact | [15 empty] | yes | NO ALARM | The point that catches a one-input arrangement wired as if it were two
25 | Synchrocheck | Synchronizer | points | 1 | In synchronism | All differences well inside their limits |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz
25 | Synchrocheck | Synchronizer | points | 2 | Angle inside limit | Angle at 80% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@9.6 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | CLOSE RELEASED | Δθ 9.6°
25 | Synchrocheck | Synchronizer | points | 3 | Angle outside limit | Angle at 120% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@14.4 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | BLOCKED | Δθ 14.4°
25 | Synchrocheck | Synchronizer | points | 4 | Voltage difference outside | Angle matched, magnitude offset past ΔV |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 50.535@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | BLOCKED | ΔV 7.20 V
25 | Synchrocheck | Synchronizer | points | 5 | Slip outside limit | Line output off frequency so the angle rotates |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | BLOCKED | Δf 0.060 Hz
25 | Synchrocheck | Synchronizer | points | 6 | Dead line, live bus | Line collapsed below the dead threshold |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | CLOSE RELEASED | From the dead-line logic
27 | Undervoltage | Voltage | pickup+time | 1 | Threshold — below | 95% of setting |  |  |  | 43.879@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate after 2.000 s
27 | Undervoltage | Voltage | pickup+time | 2 | Threshold — above | 105% of setting |  |  |  | 48.497@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
27 | Undervoltage | Voltage | pickup+time | 3 | Timing at 0.50× threshold | Step from nominal |  |  |  | 23.094@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 2.000 s | Definite time
59 | Overvoltage | Voltage | pickup+time | 1 | Threshold — above | 105% of setting |  |  |  | 69.715@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | OPERATE | Operate after 2.000 s
59 | Overvoltage | Voltage | pickup+time | 2 | Threshold — below | 95% of setting |  |  |  | 63.076@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | RESTRAIN | No operation
59 | Overvoltage | Voltage | pickup+time | 3 | Timing at 1.30× threshold | Step from nominal |  |  |  | 86.314@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 50 |  | yes | 2.000 s | Definite time
81 | Under / over frequency | Quick CMC | points | 1 | Threshold — past | 0.050 Hz beyond the setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 48.95 |  | yes | OPERATE | Operate after 0.500 s
81 | Under / over frequency | Quick CMC | points | 2 | Threshold — short of | 0.050 Hz on the healthy side |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 49.05 |  | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 3 | Timing | Step from 50.0 Hz |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 48.95 |  | yes | 0.500 s | Definite time
81 | Under / over frequency | Quick CMC | points | 4 | Below minimum voltage | Voltage under the 30 V level |  |  |  | 24.000@0.0 | 24.000@-120.0 | 24.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 48.95 |  | yes | BLOCKED | Function inhibited

## Channels (loopback)
Function | Description | Group | TU module | Drive as | # | Test step | Run | State | State label | Dur s | Channel | Magnitude | Unit | Angle deg | Hz | Note | Expected | Expected — detail | Verdict | Current at
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I A-L1 | 0.345 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I A-L2 | 0.345 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I A-L3 | 0.345 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 1 | Minimum pickup — above |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | OPERATE | Operate — no intentional delay | op
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I A-L1 | 0.255 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I A-L2 | 0.255 | A | -120 | 50 | end A | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I A-L3 | 0.255 | A | 120 | 50 | end A | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 2 | Minimum pickup — below |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I A-L1 | 0.6725 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I A-L2 | 0.6725 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I A-L3 | 0.6725 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I B-L1 | 0.3275 | A | 180 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I B-L2 | 0.3275 | A | 60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 3 | Slope at Irest 1.0 pu — above |  |  |  |  | I B-L3 | 0.3275 | A | -60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I A-L1 | 0.6275 | A | 0 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I A-L2 | 0.6275 | A | -120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I A-L3 | 0.6275 | A | 120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I B-L1 | 0.3725 | A | 180 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I B-L2 | 0.3725 | A | 60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 4 | Slope at Irest 1.0 pu — below |  |  |  |  | I B-L3 | 0.3725 | A | -60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I A-L1 | 2.0175 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I A-L2 | 2.0175 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I A-L3 | 2.0175 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I B-L1 | 0.9825 | A | 180 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I B-L2 | 0.9825 | A | 60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 5 | Slope at Irest 3.0 pu — above |  |  |  |  | I B-L3 | 0.9825 | A | -60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I A-L1 | 1.8825 | A | 0 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I A-L2 | 1.8825 | A | -120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I A-L3 | 1.8825 | A | 120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I B-L1 | 1.1175 | A | 180 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I B-L2 | 1.1175 | A | 60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 6 | Slope at Irest 3.0 pu — below |  |  |  |  | I B-L3 | 1.1175 | A | -60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I A-L1 | 5.84 | A | 0 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I A-L2 | 5.84 | A | -120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I A-L3 | 5.84 | A | 120 | 50 | end A | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I B-L1 | 2.16 | A | 180 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I B-L2 | 2.16 | A | 60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 7 | Slope at Irest 8.0 pu — above |  |  |  |  | I B-L3 | 2.16 | A | -60 | 50 | end B | OPERATE | Operate — no intentional delay | op | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I A-L1 | 5.36 | A | 0 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I A-L2 | 5.36 | A | -120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I A-L3 | 5.36 | A | 120 | 50 | end A | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I B-L1 | 2.64 | A | 180 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I B-L2 | 2.64 | A | 60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 8 | Slope at Irest 8.0 pu — below |  |  |  |  | I B-L3 | 2.64 | A | -60 | 50 | end B | RESTRAIN | No operation | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I A-L1 | 8 | A | 0 | 50 | end A | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I A-L2 | 8 | A | -120 | 50 | end A | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I A-L3 | 8 | A | 120 | 50 | end A | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I B-L1 | 8 | A | 180 | 50 | end B | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I B-L2 | 8 | A | 60 | 50 | end B | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 9 | Through-current stability |  |  |  |  | I B-L3 | 8 | A | -60 | 50 | end B | RESTRAIN | Zero differential; any standing value is a wiring or ratio error | no | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I A-L1 | 4 | A | 0 | 50 | end A | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I A-L2 | 4 | A | -120 | 50 | end A | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I A-L3 | 4 | A | 120 | 50 | end A | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I B-L1 | 4 | A | 0 | 50 | end B | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I B-L2 | 4 | A | -120 | 50 | end B | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87L | Line differential | Differential | Differential | characteristic | 10 | Internal fault |  |  |  |  | I B-L3 | 4 | A | 120 | 50 | end B | OPERATE | Idiff equals the sum of both infeeds | op | both ends
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I A-L1 | 0.115 | A | 0 | 50 | end A | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | OPERATE | Operate within 50.0 ms | op
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I A-L1 | 0.085 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I B-L1 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | RESTRAIN | No operation | no
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I A-L1 | 4 | A | 0 | 50 | end A | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I B-L1 | 4 | A | 180 | 50 | end B | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I B-L2 | 0 | A | 0 | 50 | end B | RESTRAIN | Zero residual differential | no | both ends
87N | Ground differential | Differential | Quick CMC | points | 3 | Through-current stability |  |  |  |  | I B-L3 | 0 | A | 0 | 50 | end B | RESTRAIN | Zero residual differential | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I A-L1 | 1 | A | 0 | 50 | end A | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I A-L2 | 1 | A | -120 | 50 | end A | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I A-L3 | 1 | A | 120 | 50 | end A | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I B-L1 | 0.9583 | A | 180 | 50 | end B | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I B-L2 | 0.9583 | A | 60 | 50 | end B | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 1 | Standing differential at nominal voltage |  |  |  |  | I B-L3 | 0.9583 | A | -60 | 50 | end B | NO ALARM | Compensation should reduce it to under 0.0083 pu | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I A-L1 | 1 | A | 0 | 50 | end A | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I A-L2 | 1 | A | -120 | 50 | end A | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I A-L3 | 1 | A | 120 | 50 | end A | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I B-L1 | 0.9167 | A | 180 | 50 | end B | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I B-L2 | 0.9167 | A | 60 | 50 | end B | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 2 | Over-compensation check |  |  |  |  | I B-L3 | 0.9167 | A | -60 | 50 | end B | STANDING DIFFERENTIAL | Residue 0.0417 pu even with compensation on, which is how a wrong entered value shows itself | wn | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I A-L1 | 1 | A | 0 | 50 | end A | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I A-L2 | 1 | A | -120 | 50 | end A | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I A-L3 | 1 | A | 120 | 50 | end A | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I B-L1 | 1 | A | 180 | 50 | end B | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I B-L2 | 1 | A | 60 | 50 | end B | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
Ich | Charging current compensation | Differential | Quick CMC | points | 3 | True through current |  |  |  |  | I B-L3 | 1 | A | -60 | 50 | end B | NO DIFFERENTIAL | This is the reference the other two points are measured against | no | both ends
PI | Protection interface and synchronisation | Differential | — | link / no injection | 1 | Measured delay |  |  |  |  | (no injection) |  |  |  |  | Read the delay the device reports and compare with 0.50 ms | WITHIN TOLERANCE | A reading far from the expected value means the route is not the one on the drawing | nu
PI | Protection interface and synchronisation | Differential | — | link / no injection | 2 | Asymmetry |  |  |  |  | (no injection) |  |  |  |  | Read the reported send/receive difference | UNDER 0.20 ms | Ping-pong synchronisation assumes a symmetric path — asymmetry appears directly as a phase error between the ends | nu
PI | Protection interface and synchronisation | Differential | — | link / no injection | 3 | Link interrupted |  |  |  |  | (no injection) |  |  |  |  | Disconnect the fibre or disable the channel and hold for longer than 0.100 s | 87L BLOCKS, BACKUP ARMS | Confirm the backup functions actually take over, not just that the differential drops out | op
PI | Protection interface and synchronisation | Differential | — | link / no injection | 4 | Link restored |  |  |  |  | (no injection) |  |  |  |  | Reconnect and wait for the interface to resynchronise | 87L RETURNS | Note the resynchronisation time — it is dead time on the protection | op
PI | Protection interface and synchronisation | Differential | — | link / no injection | 5 | Injection during outage |  |  |  |  | (no injection) |  |  |  |  | With the link down, apply an internal-fault current at end A | BACKUP CLEARS IT | This is the point that proves the fallback is real rather than nominal | op
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 1 | A to B, each signal |  |  |  |  | (no injection) |  |  |  |  | Assert each configured bit at end A in turn and confirm the matching output at end B | RECEIVED | One at a time — a swapped pair passes a both-at-once test | op
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 2 | B to A, each signal |  |  |  |  | (no injection) |  |  |  |  | The same in the other direction | RECEIVED | Both directions are separately configurable and separately wrong | op
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 3 | Transfer time |  |  |  |  | (no injection) |  |  |  |  | Time from assertion at one end to output at the other | ABOUT 15 ms | Against a link delay of 0.50 ms one way — the difference is device processing | nu
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 4 | Link down |  |  |  |  | (no injection) |  |  |  |  | Assert a signal with the interface disconnected | NOT RECEIVED, ALARM | The receiving end must not hold the last state as though it were live | no
85 | Intertrip over the interface | Differential | State Sequencer | sequence (assemble from these steps) | 5 | Direct transfer trip |  |  |  |  | (no injection) |  |  |  |  | Assert the DTT bit and confirm it trips the remote breaker | REMOTE TRIP | The one signal that operates plant directly — worth proving on its own, not as part of a batch | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L1 | 2.1 | A | -75 | 50 | end A | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L1 | 1.9 | A | -75 | 50 | end A | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L1 | 4 | A | -75 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50-1 | Backup overcurrent stage 1 | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I A-L1 | 1.26 | A | -75 | 50 | end A | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Long operate time — let the characteristic run out | op
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I A-L1 | 1.14 | A | -75 | 50 | end A | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L1 | 2.4 | A | -75 | 50 | end A | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 2.006 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | I A-L1 | 3.6 | A | -75 | 50 | end A | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 4 | Timing at 3.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 1.260 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | I A-L1 | 6 | A | -75 | 50 | end A | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.856 s | From the characteristic equation | nu
51 | Backup overcurrent inverse | Backup | Overcurrent | characteristic | 5 | Timing at 5.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.856 s | From the characteristic equation | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L1 | 0.42 | A | -75 | 50 | end A | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate within 0.300 s | op
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L1 | 0.38 | A | -75 | 50 | end A | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L1 | 0.8 | A | -75 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
50N-1 | Backup ground overcurrent | Backup | Overcurrent | pickup+time | 3 | Timing at 2.0× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.300 s | Measured from the current step to the trip | nu
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | I A-L1 | 2 | A | -75 | 50 | end A | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 1 | Isolator closed — stub inactive |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO STUB TRIP | 87L is in service and owns this current instead | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | I A-L1 | 1.05 | A | -75 | 50 | end A | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 2 | Isolator open — above threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | TRIP | Operate within 50.0 ms | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | I A-L1 | 0.95 | A | -75 | 50 | end A | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 3 | Isolator open — below threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO TRIP | No operation | no
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | I A-L1 | 2 | A | -75 | 50 | end A | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
Stub | Stub bus protection | Backup | Overcurrent | pickup+time | 4 | Isolator open — 87L must be out |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | STUB TRIPS, NOT 87L | Watch which function reports it, not just that something operated | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | V L1 | 57.735 | V | 0 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | V L2 | 57.735 | V | -120 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | V L3 | 57.735 | V | 120 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I A-L1 | 1 | A | -75 | 50 | end A | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I A-L2 | 1 | A | 165 | 50 | end A | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I A-L3 | 1 | A | 45 | 50 | end A | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I B-L1 | 0 | A | 0 | 50 | end B | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I B-L2 | 0 | A | 0 | 50 | end B | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Prefault load | 1 | 1/3 | Load | 2 | I B-L3 | 0 | A | 0 | 50 | end B | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | V L1 | 17.321 | V | 0 | 50 |  | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | V L2 | 17.321 | V | -120 | 50 |  | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | V L3 | 17.321 | V | 120 | 50 |  | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I A-L1 | 4 | A | -75 | 50 | end A | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I A-L2 | 4 | A | 165 | 50 | end A | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I A-L3 | 4 | A | 45 | 50 | end A | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I B-L1 | 0 | A | 0 | 50 | end B | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I B-L2 | 0 | A | 0 | 50 | end B | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Fault 1 of 1 | 1 | 2/3 | Fault 1 | 0.03 | I B-L3 | 0 | A | 0 | 50 | end B | TRIP, RECLOSE STARTED | 87L trips in 30.0 ms and sends intertrip to the far end | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | V L1 | 0 | V | 0 | 50 |  | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | V L2 | 0 | V | -120 | 50 |  | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | V L3 | 0 | V | 120 | 50 |  | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I A-L1 | 0 | A | 0 | 50 | end A | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I A-L2 | 0 | A | 0 | 50 | end A | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I A-L3 | 0 | A | 0 | 50 | end A | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I B-L1 | 0 | A | 0 | 50 | end B | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I B-L2 | 0 | A | 0 | 50 | end B | FINAL TRIP | Scheme blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Final trip | 1 | 3/3 | Final | 3 | I B-L3 | 0 | A | 0 | 50 | end B | FINAL TRIP | Scheme blocked until reset | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I A-L1 | 0.105 | A | -75 | 50 | end A | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | DETECTOR PICKED UP | Flag only | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I A-L1 | 0.095 | A | -75 | 50 | end A | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO PICKUP | Must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I A-L1 | 0.3 | A | -75 | 50 | end A | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I A-L1 | 0.3 | A | -75 | 50 | end A | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 0.250 s | Stage 2 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I A-L1 | 0 | A | -75 | 50 | end A | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | NO TRIP | Detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | NO TRIP | Detector reset stops the scheme | no
74TC | Trip circuit supervision | Automation | — | binary / DC | 1 | Healthy circuit |  |  |  |  | (no injection) |  |  |  |  | Trip circuit intact, breaker closed | NO ALARM | Both inputs energised | no
74TC | Trip circuit supervision | Automation | — | binary / DC | 2 | Trip coil open |  |  |  |  | (no injection) |  |  |  |  | Open the coil circuit at the terminal block | ALARM | After 2.000 s | op
74TC | Trip circuit supervision | Automation | — | binary / DC | 3 | Trip supply lost |  |  |  |  | (no injection) |  |  |  |  | Remove the DC supply | ALARM | After 2.000 s | op
74TC | Trip circuit supervision | Automation | — | binary / DC | 4 | Breaker open |  |  |  |  | (no injection) |  |  |  |  | Breaker open with the circuit intact | NO ALARM | The point that catches a one-input arrangement wired as if it were two | no
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V 4 | 57.735 | V | 0 | 50 | line side | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V 4 | 57.735 | V | 9.6 | 50 | line side | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | Δθ 9.6° | op
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V 4 | 57.735 | V | 14.4 | 50 | line side | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | BLOCKED | Δθ 14.4° | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V 4 | 50.535 | V | 0 | 50 | line side | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V 4 | 57.735 | V | 0 | 50.06 | line side — 50.060 Hz | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V 4 | 10 | V | 0 | 50 | line side | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | From the dead-line logic | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | CLOSE RELEASED | From the dead-line logic | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L1 | 43.879 | V | 0 | 50 | depressed phase | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L1 | 48.497 | V | 0 | 50 | depressed phase | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | V L1 | 23.094 | V | 0 | 50 | depressed phase | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.50× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 69.715 | V | 0 | 50 | raised phase | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | OPERATE | Operate after 2.000 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 63.076 | V | 0 | 50 | raised phase | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | V L1 | 86.314 | V | 0 | 50 | raised phase | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | I A-L1 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | I A-L2 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.30× threshold |  |  |  |  | I A-L3 | 0 | A | 0 | 50 | end A | 2.000 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L1 | 57.735 | V | 0 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L2 | 57.735 | V | -120 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L3 | 57.735 | V | 120 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I A-L1 | 0 | A | 0 | 48.95 | end A | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I A-L2 | 0 | A | 0 | 48.95 | end A | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I A-L3 | 0 | A | 0 | 48.95 | end A | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L1 | 57.735 | V | 0 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L2 | 57.735 | V | -120 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L3 | 57.735 | V | 120 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I A-L1 | 0 | A | 0 | 49.05 | end A | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I A-L2 | 0 | A | 0 | 49.05 | end A | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I A-L3 | 0 | A | 0 | 49.05 | end A | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L1 | 57.735 | V | 0 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L2 | 57.735 | V | -120 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L3 | 57.735 | V | 120 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I A-L1 | 0 | A | 0 | 48.95 | end A | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I A-L2 | 0 | A | 0 | 48.95 | end A | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I A-L3 | 0 | A | 0 | 48.95 | end A | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L1 | 24 | V | 0 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L2 | 24 | V | -120 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L3 | 24 | V | 120 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I A-L1 | 0 | A | 0 | 48.95 | end A | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I A-L2 | 0 | A | 0 | 48.95 | end A | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I A-L3 | 0 | A | 0 | 48.95 | end A | BLOCKED | Function inhibited | no

## Build guide
Building the 7SD82 test plan in Test Universe
A differential plan is not a list of thresholds. Almost everything a line
differential scheme fails on in service — a CT ratio entered at one end only,
a star point reversed, a fibre routed the long way round — is invisible to a
threshold test and shows up the moment current flows through the line. So the
plan is organised around **staging** first and functions second.
Read this next to the two CSV pairs:
¦ File ¦ Staging ¦ Steps ¦ Not reachable ¦
¦---¦---¦---¦---¦
¦ `7SD82-DIF-steps.csv` / `-channels.csv` ¦ local end only ¦ 69 ¦ 12 ¦
¦ `7SD82-DIF-loopback-steps.csv` / `-channels.csv` ¦ loop-back at the local end ¦ 69 ¦ 0 ¦
The injections are identical in both. Only the `Reachable` column changes.
Build from the loop-back pair if you have the second current triple; build
from the local pair if you do not, and carry the twelve unreachable steps
forward as untested rather than quietly dropping them.
---
1 · Decide the staging before you open Test Universe
Three arrangements, and they prove different things.
**Local end only.** One CMC 356 at end A, the remote device quiescent.
Reaches the local measurement path, 87L minimum pickup, 87N sensitivity,
every backup function and all the binary work. Does **not** reach the slope,
through-current stability, or CT ratio and polarity agreement between the
ends — with end B carrying nothing the operating point can only move along
Idiff = Irest, so every "slope" point you run is just the pickup test again
under a different name. Twelve steps in the plan say so.
**Loop-back at the local end.** One CMC 356 driving both current triples, the
second triple wired into the remote device's CT inputs (or into a loop that
returns to the local device where the scheme is arranged that way). This is
the practical single-set arrangement and it reaches every step in the plan.
It proves the differential characteristic and the sign convention across the
protection interface. It does not prove the field CT wiring at the remote
station, because that wiring is not in the loop.
**True end to end.** A test set at each station, GPS-synchronised, one triple
each. The only arrangement that proves the whole scheme including both sets
of field CTs. Needs two crews, two sets and a clock, so it is normally kept
for commissioning and for after a CT or fibre change.
Set the staging on the tool's Line setup tab before generating, and the plan
re-labels itself.
2 · Test object
Build the device from `Reachable`-independent data first — it does not change
with staging.
¦ Field ¦ Value from the sample ¦ Where it comes from ¦
¦---¦---¦---¦
¦ Nominal voltage, secondary ¦ 100 V L–L, 57.735 V L–N ¦ VT 110000 : 100 ¦
¦ Nominal current, secondary ¦ 1 A ¦ CT 600 : 1, both ends ¦
¦ Nominal frequency ¦ 50 Hz ¦ ¦
¦ VT ratio ¦ 1100 : 1 ¦ ¦
¦ CT ratio, end A ¦ 600 : 1 ¦ ¦
¦ CT ratio, end B ¦ 600 : 1 ¦ must match what is set in the far device ¦
¦ Reference current ¦ 600 A primary = 1 pu ¦ the base every pu value in the plan uses ¦
Enter the **end B CT ratio as it is set in the remote device**, not as the
nameplate at the remote switchyard reads. If those two disagree the scheme is
already wrong and the through-current step is what will tell you.
3 · Hardware configuration
Current amplifier: **6 × 12.5 A, two triples**. This is not optional for the
loop-back plan — every step with a value in `I_B_L1` needs a second triple.
The largest current in the plan is 8.0 A per phase per triple (the
through-current stability step), comfortably inside 12.5 A.
¦ Test set output ¦ Goes to ¦ Plan columns ¦
¦---¦---¦---¦
¦ I A / triple 1 ¦ local device CT inputs ¦ `I_L1`, `I_L2`, `I_L3` ¦
¦ I B / triple 2 ¦ remote device CT inputs ¦ `I_B_L1`, `I_B_L2`, `I_B_L3` ¦
¦ V 1–3 ¦ local device VT inputs ¦ `V_L1`, `V_L2`, `V_L3` ¦
¦ V 4 ¦ synchrocheck line side ¦ `V_4` — 25 only ¦
**Polarity is the test.** Wire triple 2 so that a through condition subtracts.
The plan expresses this as end B at 180° for a through current and at 0° for
an internal fault; if you get zero differential on the internal-fault step and
full differential on the stability step, triple 2 is reversed. Fix the wiring,
not the plan.
Binary I/O
¦ Signal ¦ Direction ¦ Used by ¦
¦---¦---¦---¦
¦ 87L trip, local ¦ input ¦ 87L, 87N, Ich ¦
¦ Intertrip receive ¦ input ¦ 85 ¦
¦ Intertrip send ¦ input ¦ 85 ¦
¦ Backup trip ¦ input ¦ 50-1, 51, 50N-1, Stub ¦
¦ Breaker-failure trip ¦ input ¦ 50BF ¦
¦ BF initiate ¦ output ¦ 50BF ¦
¦ Isolator auxiliary, stub release ¦ output ¦ Stub ¦
¦ 52a / 52b ¦ output ¦ 79, 50BF, 25 ¦
¦ Protection interface healthy ¦ input ¦ PI, and the release for 50-1 ¦
4 · Module map
`TU_Module` and `DriveAs` in the CSVs give this per step. Summarised:
¦ Function ¦ Module ¦ Notes ¦
¦---¦---¦---¦
¦ 87L ¦ Differential ¦ Enter the characteristic from the settings, then run the ten points as shots. ¦
¦ 87N ¦ Quick CMC ¦ Sensitivity on one phase; the stability point still needs both triples. ¦
¦ Ich ¦ Quick CMC ¦ Read the standing differential in DIGSI. There is no trip to time. ¦
¦ PI ¦ — ¦ Not injection. Link work, in DIGSI and at the patch panel. ¦
¦ 85 ¦ State Sequencer ¦ Time from the sending-end initiate to the receiving-end output. ¦
¦ 50-1, 51, 50N-1, Stub ¦ Overcurrent ¦ Ordinary pickup and timing. ¦
¦ 79 ¦ State Sequencer ¦ Ordered states; never split into separate shots. ¦
¦ 50BF ¦ State Sequencer ¦ Initiate is a binary output; time from its edge. ¦
¦ 74TC ¦ — ¦ Continuity at the terminal block, evidenced by the device alarm. ¦
¦ 25 ¦ Synchronizer ¦ V4 with an independent frequency for the slip case. ¦
¦ 27, 59, 81 ¦ Voltage / Quick CMC ¦ Step the frequency for 81; do not ramp it for threshold points. ¦
5 · The Differential module — 87L
Enter the characteristic once: pickup 0.30 pu, slope 1 30 % to a breakpoint of
2.0 pu restraint, slope 2 70 % beyond 6.0 pu.
Then check the **restraint definition** against DIGSI before you trust a single
slope point. The plan's per-end currents are solved from it, and the three
definitions put the device in different places for the same pair of currents:
¦ Definition ¦ Through 8 pu at each end gives Irest ¦
¦---¦---¦
¦ \¦IA\¦ + \¦IB\¦ ¦ 16.0 pu ¦
¦ max(\¦IA\¦,\¦IB\¦) ¦ 8.0 pu ¦
¦ (\¦IA\¦ + \¦IB\¦) / 2 ¦ 8.0 pu ¦
Get this wrong and every slope point lands on the wrong part of the
characteristic while still looking plausible. Change it in the tool and
re-generate; do not adjust the numbers by hand.
Run the ten steps in the order given. The order matters:
1. **Minimum pickup, above and below.** End A alone. Reachable at any staging.
2. **Slope at 1.0, 3.0 and 8.0 pu restraint**, above and below each. Both ends.
3. **Through-current stability at 8.0 pu.** Both ends, opposed.
4. **Internal fault at 4.0 pu from each end.** Both ends, in phase.
Step 3 is worth more than all the thresholds together. It is the one that
fails when something is genuinely wrong, and a standing differential there is
a wiring or ratio error, not a setting to be adjusted. Record the measured
differential even when it passes — a small standing value that grows between
visits is a CT going bad.
6 · Charging current — before you argue about a standing differential
On the sample 15 km cable the charging current is 25 A primary, which is
0.0417 pu, which is **14 % of the 0.30 pu differential threshold**. It appears
as a permanent differential on a healthy energised line.
The three Ich steps set the difference between the ends deliberately so you
can see compensation working, over-compensating, and switched off. Measure the
line's charging current, do not take it from a cable datasheet, and do not
raise the differential threshold to make a standing value go away.
7 · The protection interface
The five PI steps carry no channels on purpose. Injecting current proves
nothing about a fibre.
- Read the measured delay in DIGSI and compare it against the route on the
drawing. A reading far from expected means the fibre is not going where you
think it is.
- Read the asymmetry. Ping-pong synchronisation assumes a symmetric path, so
asymmetry appears directly as a phase error between the ends — which is to
say, as a false differential.
- Break the link. Confirm 87L blocks **and** that the backup functions
actually arm. Then inject an internal fault and confirm the backup clears
it. That last step is the one that proves the fallback is real rather than
nominal.
- Restore the link and note the resynchronisation time. It is dead time on the
protection.
8 · Before you inject
- Everything in the plan is **secondary at the device terminals**.
- Angles are degrees, counter-clockwise positive, V L1 at 0°.
- End B currents belong to the remote test set when staging is end to end, and
to triple 2 when it is loop-back.
- The sample configuration is a worked example. Enter the real line, CT and VT
data in the tool and re-generate before the plan means anything.
- Check `Reachable` on every step you are about to run.
9 · After the first build
Save the assembled plan as an OCC and re-use it. The CSVs are re-generated
from the tool whenever settings change, so the sequence of steps stays stable
and only the numbers move — re-import rather than rebuilding.
Two things the plan deliberately does not do: it does not tell you the
scheme is healthy from a local-end test, and it does not treat a standing
differential as a setting problem. Both of those are how differential schemes
get signed off and then fail on the first external fault.