## Start here
850-FDR — Multilin 850 feeder protection
How to use this workbook
Fill in | Only the two shaded columns on each test sheet: MEASURED and PASS / FAIL. Everything else is calculated and should not be edited by hand.
Example row | MEASURED "1.432 s", PASS / FAIL "PASS". Use the same unit the Expected column uses, so the two can be compared without conversion.
Untested steps | Record them as NOT TESTED with a reason. A blank result reads as work not yet done; it must never be left blank on a completed record.
If a setting changes | Do not edit numbers here. Change it in the relay tool, re-run the generator, and rebuild this workbook — that is what keeps the injected values and the calculations from drifting apart.
Where these values come from
Plan | 850-FDR — Multilin 850 feeder protection
Generated | generated 2026-09-05 12:27 from 850.html
Configuration | kv=13.8; freq=60; rot=ABC; gnd=solid; load=320; lpf=0.92; len=8; unit=mi; z1m=0.65; z1a=68; z0m=2.1; z0a=72; ctp=600; cts=5; ctc=wye; ctgp=600; ctgs=5; ctsg=50; vtp=13800; vts=120; vtc=wye; vtw=line; zsrc=I; zhold=5; k0m=0; cmc=3x; imax=32; vmax=300
Conventions | All quantities are SECONDARY at the relay terminals. Angles in degrees, CCW positive, V L1 = 0.
Sample data | Values shown are for the tool's sample configuration — re-generate after entering real station data.
Record identification
Station
Feeder / plant item
Device serial
Firmware
Setting file revision
Test set serial
Tested by
Date
Witnessed by
Sheets in this workbook
Test steps | 124 test steps — the record. Fill in MEASURED and PASS / FAIL.
Channels | 753 rows — one per channel per step, for pasting into a Test Universe module table.
Build guide | How to assemble this plan in Test Universe, and the thing about this relay most likely to be got wrong.
Progress
Total steps
Results entered
Passed
Failed
Not tested
Outstanding
Counts refer to the first test sheet only.

## Test steps
Function | Description | TU module | Drive as | # | Test step | What is applied | Run | State | Dur s | V L1 | V L2 | V L3 | V 4 | I L1 | I L2 | I L3 | Hz | Reachable | Expected | Expected — detail | MEASURED | PASS / FAIL
79 | Autoreclose | State Sequencer | sequence | 1 | Permanent — prefault load | Healthy circuit held long enough for the reclose scheme to be reset and ready | 1 | 1/5 | 2 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6667@-23.1 | 2.6667@-143.1 | 2.6667@96.9 | 60 | yes | READY | 79 reset, shot counter at zero
79 | Autoreclose | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | Faulted phase collapsed, 6.0 ×CT applied. The fault is still there on every reclose. | 1 | 2/5 | 0.08 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 30.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | TRIP, RECLOSE INITIATED | Trip in 0.080 s
79 | Autoreclose | State Sequencer | sequence | 3 | Permanent — dead time 1 | Breaker open, line dead. Dead time 1 is 0.50 s. | 1 | 3/5 | 0.5 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RECLOSE AT 0.50 s | Close output must appear at the end of this state, not before
79 | Autoreclose | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | Faulted phase collapsed, 6.0 ×CT applied. The fault is still there on every reclose. | 1 | 4/5 | 0.08 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 30.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | TRIP, SHOT 2 | Trip in 0.080 s · instantaneous now blocked, expect the time curve instead
79 | Autoreclose | State Sequencer | sequence | 5 | Permanent — lockout | After shot 2 there are no shots left. Breaker open, no further close. | 1 | 5/5 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | LOCKOUT | No close output. 79 must stay locked out until manually reset.
79 | Autoreclose | State Sequencer | sequence | 6 | Transient — prefault load | Healthy circuit, scheme reset and ready | 2 | 1/5 | 2 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6667@-23.1 | 2.6667@-143.1 | 2.6667@96.9 | 60 | yes | READY | Shot counter at zero
79 | Autoreclose | State Sequencer | sequence | 7 | Transient — fault | Single fault, cleared by the trip and gone before the reclose | 2 | 2/5 | 0.08 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 30.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | TRIP, RECLOSE INITIATED | Trip in 0.080 s
79 | Autoreclose | State Sequencer | sequence | 8 | Transient — dead time 1 | Breaker open. The fault is removed during this state. | 2 | 3/5 | 0.5 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RECLOSE AT 0.50 s | Close output at the end of the dead time
79 | Autoreclose | State Sequencer | sequence | 9 | Transient — reclaim | Load restored and held for the full reclaim time of 20.0 s | 2 | 4/5 | 20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6667@-23.1 | 2.6667@-143.1 | 2.6667@96.9 | 60 | yes | NO TRIP | Shot counter still advanced — a second fault inside this window goes to shot 2
79 | Autoreclose | State Sequencer | sequence | 10 | Transient — reset confirmed | Reclaim expired, shot counter back to zero | 2 | 5/5 | 3 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6667@-23.1 | 2.6667@-143.1 | 2.6667@96.9 | 60 | yes | RESET | A fault now must be treated as shot 1 again
CLPU | Cold load pickup | State Sequencer | sequence | 1 | Settled load | Normal load, well under pickup. Confirms the element is not armed. | 1 | 1/5 | 5 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6667@-75.0 | 2.6667@165.0 | 2.6667@45.0 | 60 | yes | NO TRIP | CLPU idle
CLPU | Cold load pickup | State Sequencer | sequence | 2 | Outage — arming | Breaker open with no current for 66 s, past the 60 s arming time. | 1 | 2/5 | 66 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | ARMS | CLPU flag picks up when the outage exceeds 60 s
CLPU | Cold load pickup | State Sequencer | sequence | 3 | Restoration inside the window | Current at 9.000 A — above the normal pickup of 6.000 A but under the lifted pickup of 12.000 A. | 1 | 3/5 | 60 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 9.0000@-75.0 | 9.0000@165.0 | 9.0000@45.0 | 60 | yes | NO TRIP | This is the point of the element. A trip here means CLPU did not arm.
CLPU | Cold load pickup | State Sequencer | sequence | 4 | Above the lifted pickup | Current raised to 13.200 A, past the lifted threshold. | 1 | 4/5 | 0.5 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 13.2000@-75.0 | 13.2000@165.0 | 13.2000@45.0 | 60 | yes | TRIP | CLPU raises the pickup, it does not disable the element
CLPU | Cold load pickup | State Sequencer | sequence | 5 | Same current after the window closes | Back to 9.000 A, held until the 120 s window expires. | 1 | 5/5 | 120 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 9.0000@-75.0 | 9.0000@165.0 | 9.0000@45.0 | 60 | yes | TRIP | The same current that was safe a moment ago must now operate
FLOC | Fault locator | Advanced Distance | shots | 1 | Fault at 10% of line | 0.80 mi out · line impedance to the fault 0.543 Ω sec |  |  |  | 4.728@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-70.5 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.80 mi | Accept 0.40 to 1.20 mi (±5.0% of line)
FLOC | Fault locator | Advanced Distance | shots | 2 | Fault at 25% of line | 2.00 mi out · line impedance to the fault 1.357 Ω sec |  |  |  | 11.819@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-70.5 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 2.00 mi | Accept 1.60 to 2.40 mi (±5.0% of line)
FLOC | Fault locator | Advanced Distance | shots | 3 | Fault at 50% of line | 4.00 mi out · line impedance to the fault 2.713 Ω sec |  |  |  | 23.639@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-70.5 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 4.00 mi | Accept 3.60 to 4.40 mi (±5.0% of line)
FLOC | Fault locator | Advanced Distance | shots | 4 | Fault at 75% of line | 6.00 mi out · line impedance to the fault 4.070 Ω sec |  |  |  | 35.458@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-70.5 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 6.00 mi | Accept 5.60 to 6.40 mi (±5.0% of line)
FLOC | Fault locator | Advanced Distance | shots | 5 | Fault at 90% of line | 7.20 mi out · line impedance to the fault 4.883 Ω sec |  |  |  | 42.549@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-70.5 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 7.20 mi | Accept 6.80 to 7.60 mi (±5.0% of line)
21 | Distance zones | Advanced Distance | shots | 1 | Zone 1 reach — inside | Fault at 72.0% of line · 5.76 mi out |  |  |  | 69.282@90.0 | 19.534@0.0 | 19.534@180.0 |  | 0.0000@0.0 | 5.0000@-68.0 | 5.0000@112.0 | 60 | yes | ZONE 1 | Operate after 0.00 s
21 | Distance zones | Advanced Distance | shots | 2 | Zone 1 reach — outside | Fault at 88.0% of line · 7.04 mi out |  |  |  | 69.282@90.0 | 23.875@0.0 | 23.875@180.0 |  | 0.0000@0.0 | 5.0000@-68.0 | 5.0000@112.0 | 60 | yes | NOT ZONE 1 | Picked up by zone 2 instead
21 | Distance zones | Advanced Distance | shots | 3 | Zone 2 reach — inside | Fault at 108.0% of line · 8.64 mi out |  |  |  | 69.282@90.0 | 29.301@0.0 | 29.301@180.0 |  | 0.0000@0.0 | 5.0000@-68.0 | 5.0000@112.0 | 60 | yes | ZONE 2 | Operate after 0.30 s
21 | Distance zones | Advanced Distance | shots | 4 | Zone 2 reach — outside | Fault at 132.0% of line · 10.56 mi out |  |  |  | 69.282@90.0 | 35.812@0.0 | 35.812@180.0 |  | 0.0000@0.0 | 5.0000@-68.0 | 5.0000@112.0 | 60 | yes | NOT ZONE 2 | Picked up by zone 3 instead
21 | Distance zones | Advanced Distance | shots | 5 | Zone 3 reach — inside | Fault at 180.0% of line · 14.40 mi out |  |  |  | 69.282@90.0 | 48.835@0.0 | 48.835@180.0 |  | 0.0000@0.0 | 5.0000@-68.0 | 5.0000@112.0 | 60 | yes | ZONE 3 | Operate after 0.80 s
21 | Distance zones | Advanced Distance | shots | 6 | Zone 3 reach — outside | Fault at 220.0% of line · 17.60 mi out |  |  |  | 69.282@90.0 | 59.687@0.0 | 59.687@180.0 |  | 0.0000@0.0 | 5.0000@-68.0 | 5.0000@112.0 | 60 | yes | NOT ZONE 3 | Picked up by no zone instead
68 | Power swing blocking | State Sequencer | sequence (assemble from these steps) | 1 | Outside the outer characteristic | Impedance at 288% of line — load territory, nothing picked up |  |  |  | 78.000@0.0 | 78.000@-120.0 | 78.000@120.0 |  | 5.0000@-68.0 | 5.0000@172.0 | 5.0000@52.0 | 60 | yes | NO PICKUP | Neither characteristic sees it
68 | Power swing blocking | State Sequencer | sequence (assemble from these steps) | 2 | Between the characteristics | Impedance at 200% — inside outer, outside inner |  |  |  | 54.261@0.0 | 54.261@-120.0 | 54.261@120.0 |  | 5.0000@-68.0 | 5.0000@172.0 | 5.0000@52.0 | 60 | yes | OUTER ONLY | The transit timer starts here
68 | Power swing blocking | State Sequencer | sequence (assemble from these steps) | 3 | Inside the inner characteristic | Impedance at 128% — both characteristics picked up |  |  |  | 34.591@0.0 | 34.591@-120.0 | 34.591@120.0 |  | 5.0000@-68.0 | 5.0000@172.0 | 5.0000@52.0 | 60 | yes | BOTH | Block asserts if the transit took longer than 30 ms
68 | Power swing blocking | State Sequencer | sequence (assemble from these steps) | 4 | Deep inside — fault territory | Impedance well inside both, reached instantly rather than by a swing |  |  |  | 16.278@0.0 | 16.278@-120.0 | 16.278@120.0 |  | 5.0000@-68.0 | 5.0000@172.0 | 5.0000@52.0 | 60 | yes | NO BLOCK | A step straight to here must not block — this is a fault
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold | 105% of the detector setting, no initiate |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.0500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | DETECTOR PICKED UP | Flag only, no trip without initiate
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold | 95% of the detector setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.9500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | NO PICKUP | Detector must drop out
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | Initiate asserted with current held and never removed |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.100 s | Timer 1 — retrip to the same breaker
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 4 | Bus trip timing | Same state, second stage |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.200 s | Timer 2 — trips the bus
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | Initiate asserted, then current removed inside timer 1 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | NO TRIP | Proves the detector reset stops the scheme
50P | Phase instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 42.000 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 42.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.02 s
50P | Phase instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 38.000 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 38.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50P | Phase instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 80.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.020 s | Measured from application of current to trip
51P | Phase time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 6.300 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.3000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51P | Phase time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 5.700 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.7000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51P | Phase time OC | Overcurrent | characteristic | 3 | Timing at 2.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Predicted from the curve equation
51P | Phase time OC | Overcurrent | characteristic | 4 | Timing at 3.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 18.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.588 s | Predicted from the curve equation
51P | Phase time OC | Overcurrent | characteristic | 5 | Timing at 5.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 30.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.262 s | Predicted from the curve equation
51P | Phase time OC | Overcurrent | characteristic | 6 | Timing at 10.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 60.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.138 s | Predicted from the curve equation
50G | Ground instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 10.500 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 10.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.02 s
50G | Ground instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 9.500 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 9.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50G | Ground instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 20.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.020 s | Measured from application of current to trip
51G | Ground time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.575 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.5750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51G | Ground time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 1.425 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.4250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51G | Ground time OC | Overcurrent | characteristic | 3 | Timing at 2.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 4 | Timing at 3.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 4.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.588 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 5 | Timing at 5.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.262 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 6 | Timing at 10.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.138 s | Predicted from the curve equation
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 10.500 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 10.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.02 s
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 9.500 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 9.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 20.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.020 s | Measured from application of current to trip
51N | Neutral time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.575 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.5750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51N | Neutral time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 1.425 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.4250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51N | Neutral time OC | Overcurrent | characteristic | 3 | Timing at 2.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Predicted from the curve equation
51N | Neutral time OC | Overcurrent | characteristic | 4 | Timing at 3.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 4.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.588 s | Predicted from the curve equation
51N | Neutral time OC | Overcurrent | characteristic | 5 | Timing at 5.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.262 s | Predicted from the curve equation
51N | Neutral time OC | Overcurrent | characteristic | 6 | Timing at 10.0× pickup | IEEE Very Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.138 s | Predicted from the curve equation
50SG | Sensitive ground IOC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 0.263 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.2625@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.02 s
50SG | Sensitive ground IOC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 0.237 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.2375@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50SG | Sensitive ground IOC | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.020 s | Measured from application of current to trip
51SG | Sensitive ground TOC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 0.105 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.1050@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51SG | Sensitive ground TOC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 0.095 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0950@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51SG | Sensitive ground TOC | Overcurrent | characteristic | 3 | Timing at 2.0× pickup | IEC Curve A (SI) · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.2000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 2.006 s | Predicted from the curve equation
51SG | Sensitive ground TOC | Overcurrent | characteristic | 4 | Timing at 3.0× pickup | IEC Curve A (SI) · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.3000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.260 s | Predicted from the curve equation
51SG | Sensitive ground TOC | Overcurrent | characteristic | 5 | Timing at 5.0× pickup | IEC Curve A (SI) · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.856 s | Predicted from the curve equation
51SG | Sensitive ground TOC | Overcurrent | characteristic | 6 | Timing at 10.0× pickup | IEC Curve A (SI) · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.594 s | Predicted from the curve equation
50_2 | Negative-sequence IOC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 2.625 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.8750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.02 s
50_2 | Negative-sequence IOC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 2.375 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.1250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50_2 | Negative-sequence IOC | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup | Step from prefault load straight to the test value |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.020 s | Measured from application of current to trip
46 | Negative-sequence TOC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.050 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.1500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
46 | Negative-sequence TOC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 0.950 A sec |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.8500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
46 | Negative-sequence TOC | Overcurrent | characteristic | 3 | Timing at 2.0× pickup | IEEE Mod Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.761 s | Predicted from the curve equation
46 | Negative-sequence TOC | Overcurrent | characteristic | 4 | Timing at 3.0× pickup | IEEE Mod Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 9.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.486 s | Predicted from the curve equation
46 | Negative-sequence TOC | Overcurrent | characteristic | 5 | Timing at 5.0× pickup | IEEE Mod Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.338 s | Predicted from the curve equation
46 | Negative-sequence TOC | Overcurrent | characteristic | 6 | Timing at 10.0× pickup | IEEE Mod Inv · TDM 0.20 |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 30.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.241 s | Predicted from the curve equation
46BC | Broken conductor | Quick CMC | points | 1 | Ratio — above threshold | I2/I1 = 22.0% · L3 reduced to 45.9% of the healthy phases |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-23.1 | 5.0000@-143.1 | 2.2951@96.9 | 60 | yes | OPERATE | Operate after 5.0 s
46BC | Broken conductor | Quick CMC | points | 2 | Ratio — below threshold | I2/I1 = 18.0% · L3 reduced to 54.2% of the healthy phases |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-23.1 | 5.0000@-143.1 | 2.7119@96.9 | 60 | yes | RESTRAIN | No operation
46BC | Broken conductor | Quick CMC | points | 3 | Fully open conductor | L3 taken to zero — the limiting case for this method, I2/I1 = 50% |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-23.1 | 5.0000@-143.1 | 0.0000@96.9 | 60 | yes | OPERATE | The deepest condition the element will ever see from a single open phase
46BC | Broken conductor | Quick CMC | points | 4 | Below minimum load | Same ratio, but total current dropped under the 0.10 ×CT supervision |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.4000@-23.1 | 0.4000@-143.1 | 0.1836@96.9 | 60 | yes | BLOCKED | Element inhibited — the ratio is meaningless at no load
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 1 | Pickup — below threshold | 95% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.4250@-23.0 | 1.4250@-143.0 | 1.4250@97.0 | 60 | yes | OPERATE | Operate after 2.0 s
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 2 | Pickup — above threshold | 105% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.5750@-23.0 | 1.5750@-143.0 | 1.5750@97.0 | 60 | yes | RESTRAIN | No operation
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 3 | Timing at half pickup | Step from normal load straight down |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.7500@-23.0 | 0.7500@-143.0 | 0.7500@97.0 | 60 | yes | 2.00 s | Definite time
37 | Undercurrent / loss of load | Overcurrent | pickup+time | 4 | Dead circuit | Current under the 0.05 ×CT block level |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.1250@-23.0 | 0.1250@-143.0 | 0.1250@97.0 | 60 | yes | BLOCKED | An open breaker must not look like loss of load
67 | Directional supervision | Ramping | points | 1 | Forward maximum torque | Current at the characteristic angle — deepest into the operate zone. |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-60.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 2 | Reverse maximum torque | Rotated 180° from MTA. |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 3 | Boundary, leading side (inside) | 5° inside the boundary. |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@25.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 4 | Boundary, leading side (outside) | 5° outside. |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@35.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 5 | Boundary, lagging side (inside) | 5° inside the boundary. |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-145.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 6 | Boundary, lagging side (outside) | 5° outside. |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-155.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup
32 | Directional power | Quick CMC | points | 1 | Above threshold | 110% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.1918@0.0 | 0.1918@-120.0 | 0.1918@120.0 | 60 | yes | OPERATE | Balanced 3φ · 550.0 kW primary
32 | Directional power | Quick CMC | points | 2 | Below threshold | 90% of setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.1569@0.0 | 0.1569@-120.0 | 0.1569@120.0 | 60 | yes | RESTRAIN | Balanced 3φ · 450.0 kW primary
32 | Directional power | Quick CMC | points | 3 | Timing at 2× pickup | Definite time |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.3486@0.0 | 0.3486@-120.0 | 0.3486@120.0 | 60 | yes | 2.0 s | Balanced 3φ · 1000.0 kW primary
27 | Undervoltage | Voltage | pickup+time | 1 | Pickup — below threshold | 95% of setting |  |  |  | 55.945@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 3.00 s
27 | Undervoltage | Voltage | pickup+time | 2 | Pickup — above threshold | 105% of setting |  |  |  | 61.834@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
27 | Undervoltage | Voltage | pickup+time | 3 | Timing at 0.60× pickup | Step from nominal to the test level |  |  |  | 35.334@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 3.00 s | Definite time
27 | Undervoltage | Voltage | pickup+time | 4 | Below minimum operating voltage | Proves the element blocks rather than operating on a dead feeder |  |  |  | 4.000@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | Element inhibited
59 | Overvoltage | Voltage | pickup+time | 1 | Pickup — above threshold | 105% of setting |  |  |  | 80.021@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 2.00 s
59 | Overvoltage | Voltage | pickup+time | 2 | Pickup — below threshold | 95% of setting |  |  |  | 72.400@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
59 | Overvoltage | Voltage | pickup+time | 3 | Timing at 1.25× pickup | Step from nominal to the test level |  |  |  | 95.263@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 2.00 s | Definite time
59N | Neutral overvoltage | Quick CMC | points | 1 | Pickup — above threshold | 3V0 = 10.50 V secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 10.500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 3.0 s
59N | Neutral overvoltage | Quick CMC | points | 2 | Pickup — below threshold | 3V0 = 9.50 V secondary |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 9.500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
59N | Neutral overvoltage | Quick CMC | points | 3 | Solid ground fault | One phase collapsed completely — 3V0 reaches the full phase voltage |  |  |  | 0.000@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | 3V0 = 69.28 V, far above any sensible setting
47 | Voltage unbalance / phase reversal | Quick CMC | points | 1 | Pickup — above threshold | Balanced set in reverse rotation — every volt applied is negative sequence |  |  |  | 7.621@0.0 | 7.621@120.0 | 7.621@-120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 5.0 s
47 | Voltage unbalance / phase reversal | Quick CMC | points | 2 | Pickup — below threshold | Balanced set in reverse rotation — every volt applied is negative sequence |  |  |  | 6.235@0.0 | 6.235@120.0 | 6.235@-120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
47 | Voltage unbalance / phase reversal | Quick CMC | points | 3 | Full phase reversal | Nominal balanced set with L2 and L3 exchanged |  |  |  | 69.282@0.0 | 69.282@120.0 | 69.282@-120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | V2 = 69.28 V
81 | Under / over frequency | Quick CMC | points | 1 | Pickup — past threshold | 0.100 Hz beyond the setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 59.2 | yes | OPERATE | Operate after 0.20 s
81 | Under / over frequency | Quick CMC | points | 2 | Pickup — short of threshold | 0.100 Hz on the healthy side |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 59.4 | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 3 | Timing | Step from 60.0 Hz straight to 59.200 Hz |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 59.2 | yes | 0.200 s | Definite time
81 | Under / over frequency | Quick CMC | points | 4 | Below minimum voltage | Frequency past the setting but voltage under the 30 V supervision level |  |  |  | 24.000@0.0 | 24.000@-120.0 | 24.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 59.2 | yes | BLOCKED | Element inhibited
81R | Rate of change of frequency | Ramping | ramp | 1 | Rate above pickup | Ramp 60.00 → 57.00 Hz at 1.200 Hz/s · 2.50 s of travel |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.15 s of sustained rate
81R | Rate of change of frequency | Ramping | ramp | 2 | Rate below pickup | Ramp 60.00 → 57.00 Hz at 0.800 Hz/s · 3.75 s of travel |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
81R | Rate of change of frequency | Ramping | ramp | 3 | Well above pickup | Ramp 60.00 → 57.00 Hz at 3.000 Hz/s · 1.00 s of travel |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.15 s of sustained rate
25 | Synchrocheck | Synchronizer | points | 1 | In synchronism | All three differences well inside their limits |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz
25 | Synchrocheck | Synchronizer | points | 2 | Angle just inside limit | Angle at 80% of the setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@16.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | CLOSE PERMITTED | Δθ 16.0°
25 | Synchrocheck | Synchronizer | points | 3 | Angle just outside limit | Angle at 120% of the setting |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@24.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | Δθ 24.0°
25 | Synchrocheck | Synchronizer | points | 4 | Voltage difference outside limit | Angle matched, magnitude offset past ΔV |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 57.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | ΔV 12.00 V
25 | Synchrocheck | Synchronizer | points | 5 | Slip outside limit | Line output run off frequency so the angle rotates |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | Δf 0.120 Hz
25 | Synchrocheck | Synchronizer | points | 6 | Dead line, live bus | Line collapsed below the dead threshold, bus healthy — the normal reclose case |  |  |  | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check
25 | Synchrocheck | Synchronizer | points | 7 | Both dead | Bus and line both below the dead threshold |  |  |  | 10.000@0.0 | 10.000@-120.0 | 10.000@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | PER SCHEME | Confirm against the scheme actually enabled

## Channels
Function | Description | Group | TU module | Drive as | # | Test step | Run | State | State label | Dur s | Channel | Magnitude | Unit | Angle deg | Hz | Note | Expected | Expected — detail | Verdict
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | V L1 | 69.282 | V | 0 | 60 |  | READY | 79 reset, shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | V L2 | 69.282 | V | -120 | 60 |  | READY | 79 reset, shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | V L3 | 69.282 | V | 120 | 60 |  | READY | 79 reset, shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | I L1 | 2.6667 | A | -23.07 | 60 |  | READY | 79 reset, shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | I L2 | 2.6667 | A | -143.07 | 60 |  | READY | 79 reset, shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | I L3 | 2.6667 | A | 96.93 | 60 |  | READY | 79 reset, shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.08 | V L1 | 69.282 | V | 0 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.08 | V L2 | 69.282 | V | -120 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.08 | V L3 | 69.282 | V | 120 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.08 | I L1 | 30 | A | -75 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.08 | I L2 | 0 | A | 0 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.08 | I L3 | 0 | A | 0 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.5 | V L1 | 0 | V | 0 | 60 |  | RECLOSE AT 0.50 s | Close output must appear at the end of this state, not before | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.5 | V L2 | 0 | V | -120 | 60 |  | RECLOSE AT 0.50 s | Close output must appear at the end of this state, not before | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.5 | V L3 | 0 | V | 120 | 60 |  | RECLOSE AT 0.50 s | Close output must appear at the end of this state, not before | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.5 | I L1 | 0 | A | 0 | 60 |  | RECLOSE AT 0.50 s | Close output must appear at the end of this state, not before | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.5 | I L2 | 0 | A | 0 | 60 |  | RECLOSE AT 0.50 s | Close output must appear at the end of this state, not before | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.5 | I L3 | 0 | A | 0 | 60 |  | RECLOSE AT 0.50 s | Close output must appear at the end of this state, not before | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.08 | V L1 | 69.282 | V | 0 | 60 |  | TRIP, SHOT 2 | Trip in 0.080 s · instantaneous now blocked, expect the time curve instead | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.08 | V L2 | 69.282 | V | -120 | 60 |  | TRIP, SHOT 2 | Trip in 0.080 s · instantaneous now blocked, expect the time curve instead | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.08 | V L3 | 69.282 | V | 120 | 60 |  | TRIP, SHOT 2 | Trip in 0.080 s · instantaneous now blocked, expect the time curve instead | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.08 | I L1 | 30 | A | -75 | 60 |  | TRIP, SHOT 2 | Trip in 0.080 s · instantaneous now blocked, expect the time curve instead | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.08 | I L2 | 0 | A | 0 | 60 |  | TRIP, SHOT 2 | Trip in 0.080 s · instantaneous now blocked, expect the time curve instead | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.08 | I L3 | 0 | A | 0 | 60 |  | TRIP, SHOT 2 | Trip in 0.080 s · instantaneous now blocked, expect the time curve instead | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 5 | Permanent — lockout | 1 | 5/5 | Lockout | 3 | V L1 | 0 | V | 0 | 60 |  | LOCKOUT | No close output. 79 must stay locked out until manually reset. | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 5 | Permanent — lockout | 1 | 5/5 | Lockout | 3 | V L2 | 0 | V | -120 | 60 |  | LOCKOUT | No close output. 79 must stay locked out until manually reset. | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 5 | Permanent — lockout | 1 | 5/5 | Lockout | 3 | V L3 | 0 | V | 120 | 60 |  | LOCKOUT | No close output. 79 must stay locked out until manually reset. | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 5 | Permanent — lockout | 1 | 5/5 | Lockout | 3 | I L1 | 0 | A | 0 | 60 |  | LOCKOUT | No close output. 79 must stay locked out until manually reset. | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 5 | Permanent — lockout | 1 | 5/5 | Lockout | 3 | I L2 | 0 | A | 0 | 60 |  | LOCKOUT | No close output. 79 must stay locked out until manually reset. | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 5 | Permanent — lockout | 1 | 5/5 | Lockout | 3 | I L3 | 0 | A | 0 | 60 |  | LOCKOUT | No close output. 79 must stay locked out until manually reset. | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | V L1 | 69.282 | V | 0 | 60 |  | READY | Shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | V L2 | 69.282 | V | -120 | 60 |  | READY | Shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | V L3 | 69.282 | V | 120 | 60 |  | READY | Shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | I L1 | 2.6667 | A | -23.07 | 60 |  | READY | Shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | I L2 | 2.6667 | A | -143.07 | 60 |  | READY | Shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | I L3 | 2.6667 | A | 96.93 | 60 |  | READY | Shot counter at zero | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.08 | V L1 | 69.282 | V | 0 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.08 | V L2 | 69.282 | V | -120 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.08 | V L3 | 69.282 | V | 120 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.08 | I L1 | 30 | A | -75 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.08 | I L2 | 0 | A | 0 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.08 | I L3 | 0 | A | 0 | 60 |  | TRIP, RECLOSE INITIATED | Trip in 0.080 s | op
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.5 | V L1 | 0 | V | 0 | 60 |  | RECLOSE AT 0.50 s | Close output at the end of the dead time | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.5 | V L2 | 0 | V | -120 | 60 |  | RECLOSE AT 0.50 s | Close output at the end of the dead time | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.5 | V L3 | 0 | V | 120 | 60 |  | RECLOSE AT 0.50 s | Close output at the end of the dead time | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.5 | I L1 | 0 | A | 0 | 60 |  | RECLOSE AT 0.50 s | Close output at the end of the dead time | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.5 | I L2 | 0 | A | 0 | 60 |  | RECLOSE AT 0.50 s | Close output at the end of the dead time | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.5 | I L3 | 0 | A | 0 | 60 |  | RECLOSE AT 0.50 s | Close output at the end of the dead time | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 20 | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | Shot counter still advanced — a second fault inside this window goes to shot 2 | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 20 | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | Shot counter still advanced — a second fault inside this window goes to shot 2 | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 20 | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | Shot counter still advanced — a second fault inside this window goes to shot 2 | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 20 | I L1 | 2.6667 | A | -23.07 | 60 |  | NO TRIP | Shot counter still advanced — a second fault inside this window goes to shot 2 | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 20 | I L2 | 2.6667 | A | -143.07 | 60 |  | NO TRIP | Shot counter still advanced — a second fault inside this window goes to shot 2 | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 20 | I L3 | 2.6667 | A | 96.93 | 60 |  | NO TRIP | Shot counter still advanced — a second fault inside this window goes to shot 2 | no
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | V L1 | 69.282 | V | 0 | 60 |  | RESET | A fault now must be treated as shot 1 again | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | V L2 | 69.282 | V | -120 | 60 |  | RESET | A fault now must be treated as shot 1 again | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | V L3 | 69.282 | V | 120 | 60 |  | RESET | A fault now must be treated as shot 1 again | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | I L1 | 2.6667 | A | -23.07 | 60 |  | RESET | A fault now must be treated as shot 1 again | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | I L2 | 2.6667 | A | -143.07 | 60 |  | RESET | A fault now must be treated as shot 1 again | nu
79 | Autoreclose | Feeder automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | I L3 | 2.6667 | A | 96.93 | 60 |  | RESET | A fault now must be treated as shot 1 again | nu
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 1 | Settled load | 1 | 1/5 | Load | 5 | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | CLPU idle | nu
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 1 | Settled load | 1 | 1/5 | Load | 5 | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | CLPU idle | nu
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 1 | Settled load | 1 | 1/5 | Load | 5 | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | CLPU idle | nu
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 1 | Settled load | 1 | 1/5 | Load | 5 | I L1 | 2.6667 | A | -75 | 60 |  | NO TRIP | CLPU idle | nu
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 1 | Settled load | 1 | 1/5 | Load | 5 | I L2 | 2.6667 | A | 165 | 60 |  | NO TRIP | CLPU idle | nu
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 1 | Settled load | 1 | 1/5 | Load | 5 | I L3 | 2.6667 | A | 45 | 60 |  | NO TRIP | CLPU idle | nu
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 2 | Outage — arming | 1 | 2/5 | Outage | 66 | V L1 | 0 | V | 0 | 60 |  | ARMS | CLPU flag picks up when the outage exceeds 60 s | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 2 | Outage — arming | 1 | 2/5 | Outage | 66 | V L2 | 0 | V | -120 | 60 |  | ARMS | CLPU flag picks up when the outage exceeds 60 s | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 2 | Outage — arming | 1 | 2/5 | Outage | 66 | V L3 | 0 | V | 120 | 60 |  | ARMS | CLPU flag picks up when the outage exceeds 60 s | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 2 | Outage — arming | 1 | 2/5 | Outage | 66 | I L1 | 0 | A | 0 | 60 |  | ARMS | CLPU flag picks up when the outage exceeds 60 s | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 2 | Outage — arming | 1 | 2/5 | Outage | 66 | I L2 | 0 | A | 0 | 60 |  | ARMS | CLPU flag picks up when the outage exceeds 60 s | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 2 | Outage — arming | 1 | 2/5 | Outage | 66 | I L3 | 0 | A | 0 | 60 |  | ARMS | CLPU flag picks up when the outage exceeds 60 s | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 3 | Restoration inside the window | 1 | 3/5 | Inrush | 60 | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | This is the point of the element. A trip here means CLPU did not arm. | no
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 3 | Restoration inside the window | 1 | 3/5 | Inrush | 60 | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | This is the point of the element. A trip here means CLPU did not arm. | no
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 3 | Restoration inside the window | 1 | 3/5 | Inrush | 60 | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | This is the point of the element. A trip here means CLPU did not arm. | no
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 3 | Restoration inside the window | 1 | 3/5 | Inrush | 60 | I L1 | 9 | A | -75 | 60 |  | NO TRIP | This is the point of the element. A trip here means CLPU did not arm. | no
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 3 | Restoration inside the window | 1 | 3/5 | Inrush | 60 | I L2 | 9 | A | 165 | 60 |  | NO TRIP | This is the point of the element. A trip here means CLPU did not arm. | no
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 3 | Restoration inside the window | 1 | 3/5 | Inrush | 60 | I L3 | 9 | A | 45 | 60 |  | NO TRIP | This is the point of the element. A trip here means CLPU did not arm. | no
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 4 | Above the lifted pickup | 1 | 4/5 | Above lifted | 0.5 | V L1 | 69.282 | V | 0 | 60 |  | TRIP | CLPU raises the pickup, it does not disable the element | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 4 | Above the lifted pickup | 1 | 4/5 | Above lifted | 0.5 | V L2 | 69.282 | V | -120 | 60 |  | TRIP | CLPU raises the pickup, it does not disable the element | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 4 | Above the lifted pickup | 1 | 4/5 | Above lifted | 0.5 | V L3 | 69.282 | V | 120 | 60 |  | TRIP | CLPU raises the pickup, it does not disable the element | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 4 | Above the lifted pickup | 1 | 4/5 | Above lifted | 0.5 | I L1 | 13.2 | A | -75 | 60 |  | TRIP | CLPU raises the pickup, it does not disable the element | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 4 | Above the lifted pickup | 1 | 4/5 | Above lifted | 0.5 | I L2 | 13.2 | A | 165 | 60 |  | TRIP | CLPU raises the pickup, it does not disable the element | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 4 | Above the lifted pickup | 1 | 4/5 | Above lifted | 0.5 | I L3 | 13.2 | A | 45 | 60 |  | TRIP | CLPU raises the pickup, it does not disable the element | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 5 | Same current after the window closes | 1 | 5/5 | Window expiry | 120 | V L1 | 69.282 | V | 0 | 60 |  | TRIP | The same current that was safe a moment ago must now operate | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 5 | Same current after the window closes | 1 | 5/5 | Window expiry | 120 | V L2 | 69.282 | V | -120 | 60 |  | TRIP | The same current that was safe a moment ago must now operate | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 5 | Same current after the window closes | 1 | 5/5 | Window expiry | 120 | V L3 | 69.282 | V | 120 | 60 |  | TRIP | The same current that was safe a moment ago must now operate | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 5 | Same current after the window closes | 1 | 5/5 | Window expiry | 120 | I L1 | 9 | A | -75 | 60 |  | TRIP | The same current that was safe a moment ago must now operate | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 5 | Same current after the window closes | 1 | 5/5 | Window expiry | 120 | I L2 | 9 | A | 165 | 60 |  | TRIP | The same current that was safe a moment ago must now operate | op
CLPU | Cold load pickup | Feeder automation | State Sequencer | sequence | 5 | Same current after the window closes | 1 | 5/5 | Window expiry | 120 | I L3 | 9 | A | 45 | 60 |  | TRIP | The same current that was safe a moment ago must now operate | op
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | V L1 | 4.728 | V | 0 | 60 | faulted phase | 0.80 mi | Accept 0.40 to 1.20 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.80 mi | Accept 0.40 to 1.20 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.80 mi | Accept 0.40 to 1.20 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | I L1 | 5 | A | -70.47 | 60 |  | 0.80 mi | Accept 0.40 to 1.20 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.80 mi | Accept 0.40 to 1.20 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.80 mi | Accept 0.40 to 1.20 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | V L1 | 11.819 | V | 0 | 60 | faulted phase | 2.00 mi | Accept 1.60 to 2.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 2.00 mi | Accept 1.60 to 2.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 2.00 mi | Accept 1.60 to 2.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | I L1 | 5 | A | -70.47 | 60 |  | 2.00 mi | Accept 1.60 to 2.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 2.00 mi | Accept 1.60 to 2.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 2.00 mi | Accept 1.60 to 2.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | V L1 | 23.639 | V | 0 | 60 | faulted phase | 4.00 mi | Accept 3.60 to 4.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 4.00 mi | Accept 3.60 to 4.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 4.00 mi | Accept 3.60 to 4.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | I L1 | 5 | A | -70.47 | 60 |  | 4.00 mi | Accept 3.60 to 4.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 4.00 mi | Accept 3.60 to 4.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 4.00 mi | Accept 3.60 to 4.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | V L1 | 35.458 | V | 0 | 60 | faulted phase | 6.00 mi | Accept 5.60 to 6.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 6.00 mi | Accept 5.60 to 6.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 6.00 mi | Accept 5.60 to 6.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | I L1 | 5 | A | -70.47 | 60 |  | 6.00 mi | Accept 5.60 to 6.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 6.00 mi | Accept 5.60 to 6.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 6.00 mi | Accept 5.60 to 6.40 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | V L1 | 42.549 | V | 0 | 60 | faulted phase | 7.20 mi | Accept 6.80 to 7.60 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 7.20 mi | Accept 6.80 to 7.60 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 7.20 mi | Accept 6.80 to 7.60 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | I L1 | 5 | A | -70.47 | 60 |  | 7.20 mi | Accept 6.80 to 7.60 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 7.20 mi | Accept 6.80 to 7.60 mi (±5.0% of line) | nu
FLOC | Fault locator | Feeder automation | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 7.20 mi | Accept 6.80 to 7.60 mi (±5.0% of line) | nu
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Zone 1 reach — inside |  |  |  |  | V L1 | 69.282 | V | 90 | 60 | healthy phase, at nominal | ZONE 1 | Operate after 0.00 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Zone 1 reach — inside |  |  |  |  | V L2 | 19.534 | V | 0 | 60 |  | ZONE 1 | Operate after 0.00 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Zone 1 reach — inside |  |  |  |  | V L3 | 19.534 | V | 180 | 60 |  | ZONE 1 | Operate after 0.00 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Zone 1 reach — inside |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | ZONE 1 | Operate after 0.00 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Zone 1 reach — inside |  |  |  |  | I L2 | 5 | A | -68 | 60 |  | ZONE 1 | Operate after 0.00 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Zone 1 reach — inside |  |  |  |  | I L3 | 5 | A | 112 | 60 |  | ZONE 1 | Operate after 0.00 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Zone 1 reach — outside |  |  |  |  | V L1 | 69.282 | V | 90 | 60 | healthy phase, at nominal | NOT ZONE 1 | Picked up by zone 2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Zone 1 reach — outside |  |  |  |  | V L2 | 23.875 | V | 0 | 60 |  | NOT ZONE 1 | Picked up by zone 2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Zone 1 reach — outside |  |  |  |  | V L3 | 23.875 | V | 180 | 60 |  | NOT ZONE 1 | Picked up by zone 2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Zone 1 reach — outside |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | NOT ZONE 1 | Picked up by zone 2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Zone 1 reach — outside |  |  |  |  | I L2 | 5 | A | -68 | 60 |  | NOT ZONE 1 | Picked up by zone 2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Zone 1 reach — outside |  |  |  |  | I L3 | 5 | A | 112 | 60 |  | NOT ZONE 1 | Picked up by zone 2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Zone 2 reach — inside |  |  |  |  | V L1 | 69.282 | V | 90 | 60 | healthy phase, at nominal | ZONE 2 | Operate after 0.30 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Zone 2 reach — inside |  |  |  |  | V L2 | 29.301 | V | 0 | 60 |  | ZONE 2 | Operate after 0.30 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Zone 2 reach — inside |  |  |  |  | V L3 | 29.301 | V | 180 | 60 |  | ZONE 2 | Operate after 0.30 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Zone 2 reach — inside |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | ZONE 2 | Operate after 0.30 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Zone 2 reach — inside |  |  |  |  | I L2 | 5 | A | -68 | 60 |  | ZONE 2 | Operate after 0.30 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Zone 2 reach — inside |  |  |  |  | I L3 | 5 | A | 112 | 60 |  | ZONE 2 | Operate after 0.30 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Zone 2 reach — outside |  |  |  |  | V L1 | 69.282 | V | 90 | 60 | healthy phase, at nominal | NOT ZONE 2 | Picked up by zone 3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Zone 2 reach — outside |  |  |  |  | V L2 | 35.812 | V | 0 | 60 |  | NOT ZONE 2 | Picked up by zone 3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Zone 2 reach — outside |  |  |  |  | V L3 | 35.812 | V | 180 | 60 |  | NOT ZONE 2 | Picked up by zone 3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Zone 2 reach — outside |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | NOT ZONE 2 | Picked up by zone 3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Zone 2 reach — outside |  |  |  |  | I L2 | 5 | A | -68 | 60 |  | NOT ZONE 2 | Picked up by zone 3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Zone 2 reach — outside |  |  |  |  | I L3 | 5 | A | 112 | 60 |  | NOT ZONE 2 | Picked up by zone 3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Zone 3 reach — inside |  |  |  |  | V L1 | 69.282 | V | 90 | 60 | healthy phase, at nominal | ZONE 3 | Operate after 0.80 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Zone 3 reach — inside |  |  |  |  | V L2 | 48.835 | V | 0 | 60 |  | ZONE 3 | Operate after 0.80 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Zone 3 reach — inside |  |  |  |  | V L3 | 48.835 | V | 180 | 60 |  | ZONE 3 | Operate after 0.80 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Zone 3 reach — inside |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | ZONE 3 | Operate after 0.80 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Zone 3 reach — inside |  |  |  |  | I L2 | 5 | A | -68 | 60 |  | ZONE 3 | Operate after 0.80 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Zone 3 reach — inside |  |  |  |  | I L3 | 5 | A | 112 | 60 |  | ZONE 3 | Operate after 0.80 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Zone 3 reach — outside |  |  |  |  | V L1 | 69.282 | V | 90 | 60 | healthy phase, at nominal | NOT ZONE 3 | Picked up by no zone instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Zone 3 reach — outside |  |  |  |  | V L2 | 59.687 | V | 0 | 60 |  | NOT ZONE 3 | Picked up by no zone instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Zone 3 reach — outside |  |  |  |  | V L3 | 59.687 | V | 180 | 60 |  | NOT ZONE 3 | Picked up by no zone instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Zone 3 reach — outside |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | NOT ZONE 3 | Picked up by no zone instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Zone 3 reach — outside |  |  |  |  | I L2 | 5 | A | -68 | 60 |  | NOT ZONE 3 | Picked up by no zone instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Zone 3 reach — outside |  |  |  |  | I L3 | 5 | A | 112 | 60 |  | NOT ZONE 3 | Picked up by no zone instead | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 1 | Outside the outer characteristic |  |  |  |  | V L1 | 78 | V | 0 | 60 |  | NO PICKUP | Neither characteristic sees it | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 1 | Outside the outer characteristic |  |  |  |  | V L2 | 78 | V | -120 | 60 |  | NO PICKUP | Neither characteristic sees it | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 1 | Outside the outer characteristic |  |  |  |  | V L3 | 78 | V | 120 | 60 |  | NO PICKUP | Neither characteristic sees it | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 1 | Outside the outer characteristic |  |  |  |  | I L1 | 5 | A | -68 | 60 |  | NO PICKUP | Neither characteristic sees it | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 1 | Outside the outer characteristic |  |  |  |  | I L2 | 5 | A | 172 | 60 |  | NO PICKUP | Neither characteristic sees it | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 1 | Outside the outer characteristic |  |  |  |  | I L3 | 5 | A | 52 | 60 |  | NO PICKUP | Neither characteristic sees it | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 2 | Between the characteristics |  |  |  |  | V L1 | 54.261 | V | 0 | 60 |  | OUTER ONLY | The transit timer starts here | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 2 | Between the characteristics |  |  |  |  | V L2 | 54.261 | V | -120 | 60 |  | OUTER ONLY | The transit timer starts here | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 2 | Between the characteristics |  |  |  |  | V L3 | 54.261 | V | 120 | 60 |  | OUTER ONLY | The transit timer starts here | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 2 | Between the characteristics |  |  |  |  | I L1 | 5 | A | -68 | 60 |  | OUTER ONLY | The transit timer starts here | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 2 | Between the characteristics |  |  |  |  | I L2 | 5 | A | 172 | 60 |  | OUTER ONLY | The transit timer starts here | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 2 | Between the characteristics |  |  |  |  | I L3 | 5 | A | 52 | 60 |  | OUTER ONLY | The transit timer starts here | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 3 | Inside the inner characteristic |  |  |  |  | V L1 | 34.591 | V | 0 | 60 |  | BOTH | Block asserts if the transit took longer than 30 ms | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 3 | Inside the inner characteristic |  |  |  |  | V L2 | 34.591 | V | -120 | 60 |  | BOTH | Block asserts if the transit took longer than 30 ms | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 3 | Inside the inner characteristic |  |  |  |  | V L3 | 34.591 | V | 120 | 60 |  | BOTH | Block asserts if the transit took longer than 30 ms | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 3 | Inside the inner characteristic |  |  |  |  | I L1 | 5 | A | -68 | 60 |  | BOTH | Block asserts if the transit took longer than 30 ms | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 3 | Inside the inner characteristic |  |  |  |  | I L2 | 5 | A | 172 | 60 |  | BOTH | Block asserts if the transit took longer than 30 ms | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 3 | Inside the inner characteristic |  |  |  |  | I L3 | 5 | A | 52 | 60 |  | BOTH | Block asserts if the transit took longer than 30 ms | op
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 4 | Deep inside — fault territory |  |  |  |  | V L1 | 16.278 | V | 0 | 60 |  | NO BLOCK | A step straight to here must not block — this is a fault | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 4 | Deep inside — fault territory |  |  |  |  | V L2 | 16.278 | V | -120 | 60 |  | NO BLOCK | A step straight to here must not block — this is a fault | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 4 | Deep inside — fault territory |  |  |  |  | V L3 | 16.278 | V | 120 | 60 |  | NO BLOCK | A step straight to here must not block — this is a fault | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 4 | Deep inside — fault territory |  |  |  |  | I L1 | 5 | A | -68 | 60 |  | NO BLOCK | A step straight to here must not block — this is a fault | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 4 | Deep inside — fault territory |  |  |  |  | I L2 | 5 | A | 172 | 60 |  | NO BLOCK | A step straight to here must not block — this is a fault | no
68 | Power swing blocking | Distance | State Sequencer | sequence (assemble from these steps) | 4 | Deep inside — fault territory |  |  |  |  | I L3 | 5 | A | 52 | 60 |  | NO BLOCK | A step straight to here must not block — this is a fault | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | I L1 | 1.05 | A | -75 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | I L1 | 0.95 | A | -75 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.100 s | Timer 1 — retrip to the same breaker | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.100 s | Timer 1 — retrip to the same breaker | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.100 s | Timer 1 — retrip to the same breaker | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L1 | 3 | A | -75 | 60 |  | 0.100 s | Timer 1 — retrip to the same breaker | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.100 s | Timer 1 — retrip to the same breaker | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.100 s | Timer 1 — retrip to the same breaker | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 4 | Bus trip timing |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.200 s | Timer 2 — trips the bus | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 4 | Bus trip timing |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.200 s | Timer 2 — trips the bus | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 4 | Bus trip timing |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.200 s | Timer 2 — trips the bus | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 4 | Bus trip timing |  |  |  |  | I L1 | 3 | A | -75 | 60 |  | 0.200 s | Timer 2 — trips the bus | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 4 | Bus trip timing |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.200 s | Timer 2 — trips the bus | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 4 | Bus trip timing |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.200 s | Timer 2 — trips the bus | nu
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L1 | 0 | A | -75 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Feeder automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.02 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.02 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 42 | A | -75 | 60 |  | OPERATE | Operate within 0.02 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 38 | A | -75 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 80 | A | -75 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L1 | 6.3 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L1 | 5.7 | A | -75 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 12 | A | -75 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L1 | 18 | A | -75 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L1 | 30 | A | -75 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L1 | 60 | A | -75 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.02 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.02 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 10.5 | A | -75 | 60 |  | OPERATE | Operate within 0.02 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 9.5 | A | -75 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 20 | A | -75 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L1 | 1.575 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L1 | 1.425 | A | -75 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 3 | A | -75 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L1 | 4.5 | A | -75 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L1 | 7.5 | A | -75 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L1 | 15 | A | -75 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.02 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.02 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 10.5 | A | -75 | 60 |  | OPERATE | Operate within 0.02 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 9.5 | A | -75 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 20 | A | -75 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L1 | 1.575 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L1 | 1.425 | A | -75 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 3 | A | -75 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L1 | 4.5 | A | -75 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L1 | 7.5 | A | -75 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L1 | 15 | A | -75 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.138 s | Predicted from the curve equation | nu
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.02 s | op
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.02 s | op
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0.2625 | A | -75 | 60 |  | OPERATE | Operate within 0.02 s | op
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0.2375 | A | -75 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 0.5 | A | -75 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50SG | Sensitive ground IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0.105 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0.095 | A | -75 | 60 |  | RESTRAIN | No operation | no
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 2.006 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 2.006 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 2.006 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 0.2 | A | -75 | 60 |  | 2.006 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 2.006 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 2.006 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 1.260 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 1.260 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 1.260 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L1 | 0.3 | A | -75 | 60 |  | 1.260 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 1.260 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 1.260 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.856 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.856 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.856 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L1 | 0.5 | A | -75 | 60 |  | 0.856 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.856 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.856 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.594 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.594 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.594 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L1 | 1 | A | -75 | 60 |  | 0.594 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.594 s | Predicted from the curve equation | nu
51SG | Sensitive ground TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.594 s | Predicted from the curve equation | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.02 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.02 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 7.875 | A | -75 | 60 |  | OPERATE | Operate within 0.02 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.02 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 7.125 | A | -75 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 15 | A | -75 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.020 s | Measured from application of current to trip | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L1 | 3.15 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L1 | 2.85 | A | -75 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.761 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.761 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.761 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L1 | 6 | A | -75 | 60 |  | 0.761 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.761 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.761 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.486 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.486 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.486 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L1 | 9 | A | -75 | 60 |  | 0.486 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.486 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.486 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.338 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.338 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.338 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L1 | 15 | A | -75 | 60 |  | 0.338 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.338 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.338 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 0.241 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 0.241 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 0.241 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L1 | 30 | A | -75 | 60 |  | 0.241 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 0.241 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10.0× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 0.241 s | Predicted from the curve equation | nu
46BC | Broken conductor | Overcurrent | Quick CMC | points | 1 | Ratio — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 1 | Ratio — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 5.0 s | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 1 | Ratio — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 5.0 s | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 1 | Ratio — above threshold |  |  |  |  | I L1 | 5 | A | -23.07 | 60 |  | OPERATE | Operate after 5.0 s | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 1 | Ratio — above threshold |  |  |  |  | I L2 | 5 | A | -143.07 | 60 |  | OPERATE | Operate after 5.0 s | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 1 | Ratio — above threshold |  |  |  |  | I L3 | 2.2951 | A | 96.93 | 60 | reduced to 45.9% of the others | OPERATE | Operate after 5.0 s | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 2 | Ratio — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 2 | Ratio — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 2 | Ratio — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 2 | Ratio — below threshold |  |  |  |  | I L1 | 5 | A | -23.07 | 60 |  | RESTRAIN | No operation | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 2 | Ratio — below threshold |  |  |  |  | I L2 | 5 | A | -143.07 | 60 |  | RESTRAIN | No operation | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 2 | Ratio — below threshold |  |  |  |  | I L3 | 2.7119 | A | 96.93 | 60 | reduced to 54.2% of the others | RESTRAIN | No operation | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 3 | Fully open conductor |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | The deepest condition the element will ever see from a single open phase | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 3 | Fully open conductor |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | The deepest condition the element will ever see from a single open phase | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 3 | Fully open conductor |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | The deepest condition the element will ever see from a single open phase | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 3 | Fully open conductor |  |  |  |  | I L1 | 5 | A | -23.07 | 60 |  | OPERATE | The deepest condition the element will ever see from a single open phase | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 3 | Fully open conductor |  |  |  |  | I L2 | 5 | A | -143.07 | 60 |  | OPERATE | The deepest condition the element will ever see from a single open phase | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 3 | Fully open conductor |  |  |  |  | I L3 | 0 | A | 96.93 | 60 | reduced to 0.0% of the others | OPERATE | The deepest condition the element will ever see from a single open phase | op
46BC | Broken conductor | Overcurrent | Quick CMC | points | 4 | Below minimum load |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Element inhibited — the ratio is meaningless at no load | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 4 | Below minimum load |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Element inhibited — the ratio is meaningless at no load | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 4 | Below minimum load |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Element inhibited — the ratio is meaningless at no load | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 4 | Below minimum load |  |  |  |  | I L1 | 0.4 | A | -23.07 | 60 |  | BLOCKED | Element inhibited — the ratio is meaningless at no load | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 4 | Below minimum load |  |  |  |  | I L2 | 0.4 | A | -143.07 | 60 |  | BLOCKED | Element inhibited — the ratio is meaningless at no load | no
46BC | Broken conductor | Overcurrent | Quick CMC | points | 4 | Below minimum load |  |  |  |  | I L3 | 0.1836 | A | 96.93 | 60 | reduced | BLOCKED | Element inhibited — the ratio is meaningless at no load | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 2.0 s | op
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 2.0 s | op
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 2.0 s | op
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L1 | 1.425 | A | -23 | 60 |  | OPERATE | Operate after 2.0 s | op
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L2 | 1.425 | A | -143 | 60 |  | OPERATE | Operate after 2.0 s | op
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L3 | 1.425 | A | 97 | 60 |  | OPERATE | Operate after 2.0 s | op
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L1 | 1.575 | A | -23 | 60 |  | RESTRAIN | No operation | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L2 | 1.575 | A | -143 | 60 |  | RESTRAIN | No operation | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L3 | 1.575 | A | 97 | 60 |  | RESTRAIN | No operation | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 2.00 s | Definite time | nu
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 2.00 s | Definite time | nu
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 2.00 s | Definite time | nu
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | I L1 | 0.75 | A | -23 | 60 |  | 2.00 s | Definite time | nu
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | I L2 | 0.75 | A | -143 | 60 |  | 2.00 s | Definite time | nu
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half pickup |  |  |  |  | I L3 | 0.75 | A | 97 | 60 |  | 2.00 s | Definite time | nu
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 4 | Dead circuit |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | An open breaker must not look like loss of load | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 4 | Dead circuit |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | An open breaker must not look like loss of load | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 4 | Dead circuit |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | An open breaker must not look like loss of load | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 4 | Dead circuit |  |  |  |  | I L1 | 0.125 | A | -23 | 60 |  | BLOCKED | An open breaker must not look like loss of load | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 4 | Dead circuit |  |  |  |  | I L2 | 0.125 | A | -143 | 60 |  | BLOCKED | An open breaker must not look like loss of load | no
37 | Undercurrent / loss of load | Overcurrent | Overcurrent | pickup+time | 4 | Dead circuit |  |  |  |  | I L3 | 0.125 | A | 97 | 60 |  | BLOCKED | An open breaker must not look like loss of load | no
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque |  |  |  |  | I L1 | 12 | A | -60 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque |  |  |  |  | I L1 | 12 | A | 120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) |  |  |  |  | I L1 | 12 | A | 25 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) |  |  |  |  | I L1 | 12 | A | 35 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) |  |  |  |  | I L1 | 12 | A | -145 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) |  |  |  |  | I L1 | 12 | A | -155 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | I L1 | 0.1918 | A | 0 | 60 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | I L2 | 0.1918 | A | -120 | 60 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | I L3 | 0.1918 | A | 120 | 60 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | I L1 | 0.1569 | A | 0 | 60 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | I L2 | 0.1569 | A | -120 | 60 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | I L3 | 0.1569 | A | 120 | 60 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | 2.0 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 2.0 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 2.0 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup |  |  |  |  | I L1 | 0.3486 | A | 0 | 60 |  | 2.0 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup |  |  |  |  | I L2 | 0.3486 | A | -120 | 60 |  | 2.0 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup |  |  |  |  | I L3 | 0.3486 | A | 120 | 60 |  | 2.0 s | Balanced 3φ · 1000.0 kW primary | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L1 | 55.945 | V | 0 | 60 | depressed phase | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 3.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L1 | 61.834 | V | 0 | 60 | depressed phase | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.60× pickup |  |  |  |  | V L1 | 35.334 | V | 0 | 60 | depressed phase | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.60× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.60× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.60× pickup |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.60× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.60× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 3.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L1 | 4 | V | 0 | 60 | depressed phase | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L1 | 80.021 | V | 0 | 60 | raised phase | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L1 | 72.4 | V | 0 | 60 | raised phase | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | V L1 | 95.263 | V | 0 | 60 | raised phase | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 3.0 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 3.0 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 3.0 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V 4 | 10.5 | V | 0 | 60 | broken-delta 3V0 input | OPERATE | Operate after 3.0 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 3.0 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 3.0 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 3.0 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V 4 | 9.5 | V | 0 | 60 | broken-delta 3V0 input | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 3 | Solid ground fault |  |  |  |  | V L1 | 0 | V | 0 | 60 | collapsed | OPERATE | 3V0 = 69.28 V, far above any sensible setting | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 3 | Solid ground fault |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | 3V0 = 69.28 V, far above any sensible setting | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 3 | Solid ground fault |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | 3V0 = 69.28 V, far above any sensible setting | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 3 | Solid ground fault |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | 3V0 = 69.28 V, far above any sensible setting | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 3 | Solid ground fault |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | 3V0 = 69.28 V, far above any sensible setting | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 3 | Solid ground fault |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | 3V0 = 69.28 V, far above any sensible setting | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L1 | 7.621 | V | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L2 | 7.621 | V | 120 | 60 |  | OPERATE | Operate after 5.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | V L3 | 7.621 | V | -120 | 60 |  | OPERATE | Operate after 5.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L1 | 6.235 | V | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L2 | 6.235 | V | 120 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | V L3 | 6.235 | V | -120 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | V2 = 69.28 V | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L2 | 69.282 | V | 120 | 60 |  | OPERATE | V2 = 69.28 V | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L3 | 69.282 | V | -120 | 60 |  | OPERATE | V2 = 69.28 V | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | OPERATE | V2 = 69.28 V | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | OPERATE | V2 = 69.28 V | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | OPERATE | V2 = 69.28 V | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 59.2 |  | OPERATE | Operate after 0.20 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 59.2 |  | OPERATE | Operate after 0.20 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 59.2 |  | OPERATE | Operate after 0.20 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | I L1 | 0 | A | 0 | 59.2 |  | OPERATE | Operate after 0.20 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | I L2 | 0 | A | 0 | 59.2 |  | OPERATE | Operate after 0.20 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold |  |  |  |  | I L3 | 0 | A | 0 | 59.2 |  | OPERATE | Operate after 0.20 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | V L1 | 69.282 | V | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | V L2 | 69.282 | V | -120 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | V L3 | 69.282 | V | 120 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | I L1 | 0 | A | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | I L2 | 0 | A | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold |  |  |  |  | I L3 | 0 | A | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L1 | 69.282 | V | 0 | 59.2 |  | 0.200 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L2 | 69.282 | V | -120 | 59.2 |  | 0.200 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L3 | 69.282 | V | 120 | 59.2 |  | 0.200 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L1 | 0 | A | 0 | 59.2 |  | 0.200 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L2 | 0 | A | 0 | 59.2 |  | 0.200 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L3 | 0 | A | 0 | 59.2 |  | 0.200 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L1 | 24 | V | 0 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L2 | 24 | V | -120 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L3 | 24 | V | 120 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L1 | 0 | A | 0 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L2 | 0 | A | 0 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L3 | 0 | A | 0 | 59.2 |  | BLOCKED | Element inhibited | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 | ramp to 57.00 Hz over 2.50 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 | ramp to 57.00 Hz over 2.50 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 | ramp to 57.00 Hz over 2.50 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup |  |  |  |  | I L1 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 2.50 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 2.50 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 2.50 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 | ramp to 57.00 Hz over 3.75 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 | ramp to 57.00 Hz over 3.75 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 | ramp to 57.00 Hz over 3.75 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup |  |  |  |  | I L1 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 3.75 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 3.75 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 3.75 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup |  |  |  |  | V L1 | 69.282 | V | 0 | 60 | ramp to 57.00 Hz over 1.00 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup |  |  |  |  | V L2 | 69.282 | V | -120 | 60 | ramp to 57.00 Hz over 1.00 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup |  |  |  |  | V L3 | 69.282 | V | 120 | 60 | ramp to 57.00 Hz over 1.00 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup |  |  |  |  | I L1 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 1.00 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup |  |  |  |  | I L2 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 1.00 s | OPERATE | Operate after 0.15 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup |  |  |  |  | I L3 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 1.00 s | OPERATE | Operate after 0.15 s of sustained rate | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism |  |  |  |  | V 4 | 69.282 | V | 0 | 60 | line side | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit |  |  |  |  | V 4 | 69.282 | V | 16 | 60 | line side | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit |  |  |  |  | V 4 | 69.282 | V | 24 | 60 | line side | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit |  |  |  |  | V 4 | 57.282 | V | 0 | 60 | line side | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V 4 | 69.282 | V | 0 | 60.12 | line side — 60.120 Hz | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L1 | 69.282 | V | 0 | 60 |  | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L2 | 69.282 | V | -120 | 60 |  | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L3 | 69.282 | V | 120 | 60 |  | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V 4 | 10 | V | 0 | 60 | line side | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Permissive comes from the dead-line logic, not from sync check | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead |  |  |  |  | V L1 | 10 | V | 0 | 60 |  | PER SCHEME | Confirm against the scheme actually enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead |  |  |  |  | V L2 | 10 | V | -120 | 60 |  | PER SCHEME | Confirm against the scheme actually enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead |  |  |  |  | V L3 | 10 | V | 120 | 60 |  | PER SCHEME | Confirm against the scheme actually enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead |  |  |  |  | V 4 | 10 | V | 0 | 60 | line side | PER SCHEME | Confirm against the scheme actually enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead |  |  |  |  | I L1 | 0 | A | 0 | 60 |  | PER SCHEME | Confirm against the scheme actually enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead |  |  |  |  | I L2 | 0 | A | 0 | 60 |  | PER SCHEME | Confirm against the scheme actually enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead |  |  |  |  | I L3 | 0 | A | 0 | 60 |  | PER SCHEME | Confirm against the scheme actually enabled | nu

## Build guide
Building the 850 OCC in Test Universe
Assembles `850-FDR-steps.csv` and `850-FDR-channels.csv` into one Test Universe document.
Work through it once, save the result as a template, and every subsequent 850 becomes a
re-point of the test object rather than a rebuild.
Values below are for the tool's **sample** feeder — 13.8 kV, 8 miles, 0.65 Ω/mi ∠68°, CT 600:5,
VT 13800:120. Enter your real data in `850.html`, re-run the generator, and the numbers change
underneath you. The header comment in each CSV records which configuration produced it.
---
1 · Test object
Test Universe references everything through the test object, so this comes first.
If OMICRON publish an XRIO converter for the 8 Series, use it — it maps the relay's own setting
names and is worth more than a hand-built object. Otherwise create a generic test object and
fill in:
¦ Field ¦ Sample value ¦ Where it comes from ¦
¦-------¦--------------¦---------------------¦
¦ Nominal voltage, secondary ¦ 120 V L–L (69.282 V L–N) ¦ VT secondary ¦
¦ Nominal current, secondary ¦ 5 A ¦ CT secondary ¦
¦ VT ratio ¦ 13800 : 120 = 115 : 1 ¦ VT schedule ¦
¦ CT ratio ¦ 600 : 5 = 120 : 1 ¦ CT schedule ¦
¦ Nominal frequency ¦ 60 Hz ¦ ¦
¦ Line angle ¦ 68° ¦ Z1 angle ¦
¦ Z1 secondary ¦ 5.426 Ω ¦ `z1m × len × CTR/VTR` ¦
¦ Z0 secondary ¦ 17.530 Ω ¦ same conversion ¦
¦ k0 ¦ 0.7448 ∠5.79° ¦ `(Z0 − Z1) / 3Z1` ¦
The k0 value is the one worth double-checking against the relay's own setting. It is also the
one that makes ground reaches measure wrong while every phase reach measures right.
2 · Hardware configuration
**Amplifier mode: 3 × 32 A.** A feeder relay has one CT set, so nothing is gained by splitting
into two triples, and the 32 A channel limit is what makes the instantaneous elements testable —
50P at 8 ×CT is 40 A, which needs attention either way (see §7).
Voltage: three phases plus **V 4** for the line-side input. The synchrocheck slip test needs V 4
running at an independent frequency, so declare it as a separate generator rather than a copy of
V L1.
Binary I/O
¦ CMC ¦ Direction ¦ To / from the relay ¦
¦-----¦-----------¦---------------------¦
¦ Bin. in 1 ¦ in ¦ Trip contact — the timing reference for every operate time ¦
¦ Bin. in 2 ¦ in ¦ Close output — reclose, and the 25 permissive ¦
¦ Bin. in 3 ¦ in ¦ Pickup / start flag, where the relay offers one ¦
¦ Bin. out 1 ¦ out ¦ 52a breaker simulation ¦
¦ Bin. out 2 ¦ out ¦ 52b breaker simulation ¦
¦ Bin. out 3 ¦ out ¦ Breaker failure initiate (BFI) ¦
The 52a/52b pair is not optional for the reclose work. The scheme tracks breaker position to know
whether its close took; without it the relay declares a close failure part-way through and the
later shots never run.
3 · Module map
Filter `850-FDR-steps.csv` on the `TU_Module` column. Each group below becomes one module in the
document, in this order — it puts the quick checks first and the long sequences last, which is
also the order you want if the outage gets cut short.
¦ Order ¦ Module ¦ Elements ¦ Steps ¦
¦------:¦--------¦----------¦------:¦
¦ 1 ¦ Overcurrent — pickup + time ¦ 50P, 50G, 50N, 50SG, 50_2, 37 ¦ 19 ¦
¦ 2 ¦ Overcurrent — characteristic ¦ 51P, 51G, 51N, 51SG, 46 ¦ 30 ¦
¦ 3 ¦ Voltage ¦ 27, 59 ¦ 7 ¦
¦ 4 ¦ Quick CMC ¦ 32, 46BC, 47, 59N, 81 ¦ 17 ¦
¦ 5 ¦ Ramping ¦ 67 (6 points), 81R (3 ramps) ¦ 9 ¦
¦ 6 ¦ Synchronizer ¦ 25 ¦ 7 ¦
¦ 7 ¦ Advanced Distance ¦ 21, FLOC ¦ 11 ¦
¦ 8 ¦ State Sequencer ¦ 79, CLPU (15 sequenced) · 50BF, 68 (9 assembled) ¦ 24 ¦
4 · Overcurrent modules
Pickup rows come in pairs — one above the threshold that must operate and one below that must
not. Enter the pair, not just the operate point; a relay that trips on both tells you nothing and
a relay that trips on neither looks identical to one that is out of service.
For the characteristic tests, the `Expected` column carries the predicted operate time from the
curve equation. **Check the first one against the relay's own prediction before accepting the
rest** — curve constants have moved between firmware revisions, and if the first point disagrees
every other time in the table is wrong by the same factor.
Negative-sequence rows (50_2, 46) already carry the ×3 that a single-phase injection needs to
produce the intended I2. Do not apply it again.
Sensitive-ground rows (50SG, 51SG) go **through the core-balance window**, not into a phase CT.
A lead routed back through the window the wrong way inverts the result.
5 · Advanced Distance — 21 and FLOC
Both elements place a fault at a position on the line rather than at a current. Enter each row as
a shot; the `WhatIsApplied` column gives the position as a percentage and a distance.
The loop matters. 21 defaults to the phase loop (tested L2–L3, no k0) and FLOC to A–G (k0
compensated). Run **both** loops at the same positions if you can: matching phase results with
drifting ground results points at k0 or Z0, not at the relay.
For FLOC read the relay's own reported distance out of its fault record. There is no trip to time
— the element is a measurement, and the `Expected` column is the acceptance window around the
true position.
6 · State Sequencer — the four sequences
These are the ones worth building carefully. Filter on `SeqRun` and `SeqState`; each run is one
sequence and the states go in in order.
**79 autoreclose — two runs.** Run 1 is a permanent fault that must spend both shots and reach
lockout; run 2 is a transient that must reclose once and reset. Ten states between them. Drive
the transitions from the relay's own trip and close outputs with the breaker simulated, not from
fixed times — the point of the test is that the relay decides when things happen.
**CLPU cold load pickup — one run, five states.** Everything turns on one current sitting between
the normal pickup (6.000 A) and the lifted pickup (12.000 A): **9.000 A**. It must not trip while
the window is open and must trip once it closes. If it behaves the same in both states the
element is doing nothing. The arming and window timers run to minutes; shorten them in the relay
for the test and record as-found and as-left.
**50BF breaker failure — assemble from its five steps.** Listed as points but only meaningful in
order: detector above, detector below, retrip timing, backup timing, and the reset check. Timers
start from the BFI edge on binary output 3, not from the current step. The reset check is the one
that matters in service — a slow detector reset trips the bus on every successful clearance.
**68 power swing blocking — assemble from its four steps.** The static points only locate the two
characteristics. The discrimination is the transit time between them: step 1 → 2 → 3 with more
than 30 ms between transitions should block, and a step straight from 1 to 4 must not.
7 · Before you inject
Two things in the sample configuration are worth resolving first, and both will show up in your
own data too:
- **50P at 8 ×CT is 40 A secondary**, past the 32 A channel limit. Either drop the test multiple
and note it, or prove the pickup at a reduced multiple and the timing separately. The tool
flags this per-row; the CSV carries the values regardless, so check the `Magnitude` column
before building the module.
- **51P timing at higher multiples** climbs quickly. Confirm each row against the channel limit
rather than discovering it mid-run.
8 · After the first build
Save as a template with the test object detached, so the next 850 is: open template → point at
the new test object → re-run the generator → paste. The module structure, binary map and
sequence shapes do not change between feeders. Only the numbers do.