## Start here
7SJ85-SIP — Siemens 7SJ85 SIPROTEC 5 overcurrent
How to use this workbook
Fill in | Only the two shaded columns on each test sheet: MEASURED and PASS / FAIL. Everything else is calculated and should not be edited by hand.
Example row | MEASURED "1.432 s", PASS / FAIL "PASS". Use the same unit the Expected column uses, so the two can be compared without conversion.
Untested steps | Record them as NOT TESTED with a reason. A blank result reads as work not yet done; it must never be left blank on a completed record.
If a setting changes | Do not edit numbers here. Change it in the relay tool, re-run the generator, and rebuild this workbook — that is what keeps the injected values and the calculations from drifting apart.
Where these values come from
Plan | 7SJ85-SIP — Siemens 7SJ85 SIPROTEC 5 overcurrent
Generated | generated 2026-09-15 01:41 from src/7sj85-sip.html
Configuration | kv=20; freq=50; rot=ABC; gnd=res; load=180; lpf=0.9; len=12; unit=km; z1m=0.12; z1a=72; z0m=0.38; z0a=68; ctp=400; cts=1; ctstar=line; ctgp=60; ctgs=1; i0src=cb; vtp=20000; vts=100; vtc=wye; v0src=bd; bdr=100; zsrc=I; zhold=1; cmc=3x; imax=32; vmax=300
Conventions | All quantities are SECONDARY at the relay terminals. Angles in degrees, CCW positive, V L1 = 0.
Sample data | Values shown are for the tool's sample configuration — re-generate after entering real station data.
Record identification
Station
Feeder / plant item
Device serial
Firmware
Setting file revision
Test set serial
Tested by
Date
Witnessed by
Sheets in this workbook
Test steps | 125 test steps — the record. Fill in MEASURED and PASS / FAIL.
Channels | 770 rows — one per channel per step, for pasting into a Test Universe module table.
Build guide | How to assemble this plan in Test Universe, and the thing about this relay most likely to be got wrong.
Progress
Total steps
Results entered
Passed
Failed
Not tested
Outstanding
Counts refer to the first test sheet only.

## Test steps
Function | Description | TU module | Drive as | # | Test step | What is applied | Run | State | Dur s | V L1 | V L2 | V L3 | V 4 | I L1 | I L2 | I L3 | Hz | Reachable | Expected | Expected — detail | MEASURED | PASS / FAIL
67Ns | Sensitive directional ground fault | Quick CMC | points | 1 | Forward — full component | Residual current aligned with the measured axis, so the whole active component is available |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Component 60.0 mA against a 15.0 mA threshold
67Ns | Sensitive directional ground fault | Quick CMC | points | 2 | Reverse | Rotated 180° — the component reverses sign |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation in the reverse half-plane
67Ns | Sensitive directional ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) | 8° inside the 75.5° edge · component 22.9 mA |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Component still above the 15.0 mA threshold
67Ns | Sensitive directional ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) | 8° past the edge · component 6.8 mA |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | Component has fallen under the threshold
67Ns | Sensitive directional ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) | 8° inside the 75.5° edge |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Component still above threshold
67Ns | Sensitive directional ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) | 8° past the edge |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | Component has fallen under the threshold
67Ns | Sensitive directional ground fault | Quick CMC | points | 7 | Component — above threshold | Aligned with the axis at 120% of the component threshold |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate after 1.000 s
67Ns | Sensitive directional ground fault | Quick CMC | points | 8 | Component — below threshold | Aligned with the axis at 80% of the component threshold |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
67Ns | Sensitive directional ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn | 3V0 dropped under the 20.0 V threshold with the current unchanged |  |  |  | 48.497@0.0 | 62.865@-127.3 | 62.865@127.3 | 16.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | BLOCKED | The function has no reference to measure against
67Ns | Sensitive directional ground fault | Quick CMC | points | 10 | Residual current below threshold | Aligned with the axis but under the 10.0 mA current threshold |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | BLOCKED | Magnitude supervision holds it off
59N | Displacement voltage | Quick CMC | points | 1 | Threshold — above | 110% of the 20.0 V setting |  |  |  | 45.033@0.0 | 65.023@-129.7 | 65.023@129.7 | 22.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate after 3.000 s
59N | Displacement voltage | Quick CMC | points | 2 | Threshold — below | 90% of the 20.0 V setting |  |  |  | 47.343@0.0 | 63.571@-128.1 | 63.571@128.1 | 18.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
59N | Displacement voltage | Quick CMC | points | 3 | Reset check | Dropped just under the 0.95 × reset ratio after operating |  |  |  | 46.985@0.0 | 63.793@-128.4 | 63.793@128.4 | 18.620@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESETS | Approach this one from above, having already picked up
59N | Displacement voltage | Quick CMC | points | 4 | Fault at 25% displacement | Neutral shifted 25% — a fault through 3.0× the network zero-sequence impedance |  |  |  | 43.301@0.0 | 66.144@-130.9 | 66.144@130.9 | 25.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V
59N | Displacement voltage | Quick CMC | points | 5 | Fault at 50% displacement | Neutral shifted 50% — a fault through 1.0× the network zero-sequence impedance |  |  |  | 28.868@0.0 | 76.376@-139.1 | 76.376@139.1 | 50.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V
59N | Displacement voltage | Quick CMC | points | 6 | Fault at 100% displacement | Neutral shifted 100% — a solid ground fault |  |  |  | 0.000@0.0 | 100.000@-150.0 | 100.000@150.0 | 100.000@180.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V
50-1 | Overcurrent stage 1 | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting · operating quantity 2.6250 A |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.6250@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate within 0.100 s
50-1 | Overcurrent stage 1 | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting · operating quantity 2.3750 A |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.3750@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
50-1 | Overcurrent stage 1 | Overcurrent | pickup+time | 3 | Timing at 2× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 5.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.100 s | Measured from the current step to the trip
50-2 | Overcurrent stage 2 | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting · operating quantity 8.4000 A |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 8.4000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate within 0.100 s
50-2 | Overcurrent stage 2 | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting · operating quantity 7.6000 A |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 7.6000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
50-2 | Overcurrent stage 2 | Overcurrent | pickup+time | 3 | Timing at 2× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 16.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.100 s | Measured from the current step to the trip
51 | Overcurrent inverse time | Overcurrent | characteristic | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.2600@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Long operate time — let the characteristic run out
51 | Overcurrent inverse time | Overcurrent | characteristic | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.1400@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
51 | Overcurrent inverse time | Overcurrent | characteristic | 3 | Timing at 2× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 2.006 s | From the characteristic equation
51 | Overcurrent inverse time | Overcurrent | characteristic | 4 | Timing at 3× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 3.6000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 1.260 s | From the characteristic equation
51 | Overcurrent inverse time | Overcurrent | characteristic | 5 | Timing at 5× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 6.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.856 s | From the characteristic equation
51 | Overcurrent inverse time | Overcurrent | characteristic | 6 | Timing at 10× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 12.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.594 s | From the characteristic equation
50N-1 | Ground overcurrent stage 1 | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting · operating quantity 420.0 mA |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate within 0.100 s
50N-1 | Ground overcurrent stage 1 | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting · operating quantity 380.0 mA |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
50N-1 | Ground overcurrent stage 1 | Overcurrent | pickup+time | 3 | Timing at 2× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.100 s | Measured from the current step to the trip
50N-2 | Ground overcurrent stage 2 | Overcurrent | pickup+time | 1 | Threshold — above | 105% of setting · operating quantity 2.1000 A |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate within 0.100 s
50N-2 | Ground overcurrent stage 2 | Overcurrent | pickup+time | 2 | Threshold — below | 95% of setting · operating quantity 1.9000 A |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
50N-2 | Ground overcurrent stage 2 | Overcurrent | pickup+time | 3 | Timing at 2× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.100 s | Measured from the current step to the trip
51N | Ground inverse time | Overcurrent | characteristic | 1 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Long operate time — let the characteristic run out
51N | Ground inverse time | Overcurrent | characteristic | 2 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
51N | Ground inverse time | Overcurrent | characteristic | 3 | Timing at 2× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 2.006 s | From the characteristic equation
51N | Ground inverse time | Overcurrent | characteristic | 4 | Timing at 3× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 1.260 s | From the characteristic equation
51N | Ground inverse time | Overcurrent | characteristic | 5 | Timing at 5× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.856 s | From the characteristic equation
51N | Ground inverse time | Overcurrent | characteristic | 6 | Timing at 10× threshold | IEC Normal Inverse · T = 0.20 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.594 s | From the characteristic equation
46 | Unbalanced load | Overcurrent | characteristic | 1 | Threshold — above | 105% of setting · operating quantity 315.0 mA |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.9450@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate within 0.100 s
46 | Unbalanced load | Overcurrent | characteristic | 2 | Threshold — below | 95% of setting · operating quantity 285.0 mA |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.8550@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
46 | Unbalanced load | Overcurrent | characteristic | 3 | Timing at 2× threshold | Step from prefault load straight to the test value |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.8000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.100 s | Measured from the current step to the trip
Inrush | 2nd harmonic inrush restraint | Harmonics | points | 1 | Harmonic above threshold | 17.3% content — the device should read this as inrush |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 3.0000@0.0 |  |  | 50 | yes | BLOCKED | Overcurrent stages held off
Inrush | 2nd harmonic inrush restraint | Harmonics | points | 2 | Harmonic below threshold | 12.8% content — not enough to look like inrush |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 3.0000@0.0 |  |  | 50 | yes | OPERATE | The overcurrent stage is released and trips
Inrush | 2nd harmonic inrush restraint | Harmonics | points | 3 | No harmonic | Clean fundamental only — a genuine fault |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 3.0000@0.0 |  |  | 50 | yes | OPERATE | This is the case an ordinary overcurrent test produces
Inrush | 2nd harmonic inrush restraint | Harmonics | points | 4 | Above the upper limit | Harmonic still present but fundamental raised past the 8.0 × In release level |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 9.6000@0.0 |  |  | 50 | yes | OPERATE | Blocking is abandoned above the upper limit — a real fault does not wait for the harmonic to clear
21 | Distance zones | Advanced Distance | shots | 1 | Z1 reach — inside | Fault at 76.5% of line · 9.18 km out |  |  |  | 57.735@90.0 | 28.951@-85.6 | 28.951@-94.4 |  | 0.0000@0.0 | 1.0000@-72.0 | 1.0000@108.0 | 50 | yes | ZONE 1 | Operate after 0.000 s
21 | Distance zones | Advanced Distance | shots | 2 | Z1 reach — outside | Fault at 93.5% of line · 11.22 km out |  |  |  | 57.735@90.0 | 28.993@-84.7 | 28.993@-95.3 |  | 0.0000@0.0 | 1.0000@-72.0 | 1.0000@108.0 | 50 | yes | NOT ZONE 1 | Picked up by Z2 instead
21 | Distance zones | Advanced Distance | shots | 3 | Z2 reach — inside | Fault at 108.0% of line · 12.96 km out |  |  |  | 57.735@90.0 | 29.035@-83.9 | 29.035@-96.1 |  | 0.0000@0.0 | 1.0000@-72.0 | 1.0000@108.0 | 50 | yes | ZONE 2 | Operate after 0.300 s
21 | Distance zones | Advanced Distance | shots | 4 | Z2 reach — outside | Fault at 132.0% of line · 15.84 km out |  |  |  | 57.735@90.0 | 29.117@-82.5 | 29.117@-97.5 |  | 0.0000@0.0 | 1.0000@-72.0 | 1.0000@108.0 | 50 | yes | NOT ZONE 2 | Picked up by Z3 instead
21 | Distance zones | Advanced Distance | shots | 5 | Z3 reach — inside | Fault at 180.0% of line · 21.60 km out |  |  |  | 57.735@90.0 | 29.329@-79.8 | 29.329@-100.2 |  | 0.0000@0.0 | 1.0000@-72.0 | 1.0000@108.0 | 50 | yes | ZONE 3 | Operate after 0.900 s
21 | Distance zones | Advanced Distance | shots | 6 | Z3 reach — outside | Fault at 220.0% of line · 26.40 km out |  |  |  | 57.735@90.0 | 29.555@-77.6 | 29.555@-102.4 |  | 0.0000@0.0 | 1.0000@-72.0 | 1.0000@108.0 | 50 | yes | NOT ZONE 3 | No zone sees it
FLOC | Fault locator | Advanced Distance | shots | 1 | Fault at 10% of line | 1.20 km out · line impedance to the fault 0.288 Ω sec |  |  |  | 0.496@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@-69.5 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 1.20 km | Accept 0.60 to 1.80 km
FLOC | Fault locator | Advanced Distance | shots | 2 | Fault at 25% of line | 3.00 km out · line impedance to the fault 0.720 Ω sec |  |  |  | 1.239@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@-69.5 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 3.00 km | Accept 2.40 to 3.60 km
FLOC | Fault locator | Advanced Distance | shots | 3 | Fault at 50% of line | 6.00 km out · line impedance to the fault 1.440 Ω sec |  |  |  | 2.479@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@-69.5 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 6.00 km | Accept 5.40 to 6.60 km
FLOC | Fault locator | Advanced Distance | shots | 4 | Fault at 75% of line | 9.00 km out · line impedance to the fault 2.160 Ω sec |  |  |  | 3.718@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@-69.5 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 9.00 km | Accept 8.40 to 9.60 km
FLOC | Fault locator | Advanced Distance | shots | 5 | Fault at 90% of line | 10.80 km out · line impedance to the fault 2.592 Ω sec |  |  |  | 4.461@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.0000@-69.5 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 10.80 km | Accept 10.20 to 11.40 km
67 | Directional overcurrent | Ramping | points | 1 | Forward — maximum torque | Current on the characteristic axis, deepest into the forward sector. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@-45.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | FORWARD | Current held at 2.0× threshold
67 | Directional overcurrent | Ramping | points | 2 | Reverse — maximum torque | Rotated 180° from the axis. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@135.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | REVERSE | Current held at 2.0× threshold
67 | Directional overcurrent | Ramping | points | 3 | Boundary, leading (inside) | 5° inside the sector edge. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@40.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | FORWARD | Current held at 2.0× threshold
67 | Directional overcurrent | Ramping | points | 4 | Boundary, leading (outside) | 5° past the edge. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@50.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | REVERSE | Current held at 2.0× threshold
67 | Directional overcurrent | Ramping | points | 5 | Boundary, lagging (inside) | 5° inside the sector edge. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@-130.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | FORWARD | Current held at 2.0× threshold
67 | Directional overcurrent | Ramping | points | 6 | Boundary, lagging (outside) | 5° past the edge. |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.4000@-140.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | REVERSE | Current held at 2.0× threshold
49 | Thermal overload | Overcurrent | characteristic | 1 | Operate at 1.5× k·In | Applied 1.6500 A · preload 0.90× k·In |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.6500@-26.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 2.83 min | Alarm at 2.55 min
49 | Thermal overload | Overcurrent | characteristic | 2 | Operate at 2× k·In | Applied 2.2000 A · preload 0.90× k·In |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 2.2000@-26.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 73.69 s | Alarm at 66.32 s
49 | Thermal overload | Overcurrent | characteristic | 3 | Operate at 3× k·In | Applied 3.3000 A · preload 0.90× k·In |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 3.3000@-26.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 28.17 s | Alarm at 25.35 s
49 | Thermal overload | Overcurrent | characteristic | 4 | Operate at 5× k·In | Applied 5.5000 A · preload 0.90× k·In |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 5.5000@-26.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 9.463 s | Alarm at 8.516 s
37 | Undercurrent | Overcurrent | pickup+time | 1 | Threshold — below | 95% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.1900@-26.0 | 0.1900@-146.0 | 0.1900@94.0 | 50 | yes | OPERATE | Operate after 3.000 s
37 | Undercurrent | Overcurrent | pickup+time | 2 | Threshold — above | 105% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.2100@-26.0 | 0.2100@-146.0 | 0.2100@94.0 | 50 | yes | RESTRAIN | No operation
37 | Undercurrent | Overcurrent | pickup+time | 3 | Timing at half threshold | Step from full load straight down |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.1000@-26.0 | 0.1000@-146.0 | 0.1000@94.0 | 50 | yes | 3.000 s | Definite time
37 | Undercurrent | Overcurrent | pickup+time | 4 | Open circuit | Under the 0.03 × In block level |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0150@-26.0 | 0.0150@-146.0 | 0.0150@94.0 | 50 | yes | BLOCKED | An open breaker must not read as lost load
51V | Voltage-dependent overcurrent | Quick CMC | points | 1 | V = 1 ×Vn — above threshold | Effective threshold 1.5000 A at 57.74 V |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.5750@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Characteristic runs from here
51V | Voltage-dependent overcurrent | Quick CMC | points | 2 | V = 1 ×Vn — below threshold | Effective threshold 1.5000 A at 57.74 V |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 1.4250@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
51V | Voltage-dependent overcurrent | Quick CMC | points | 3 | V = 0.75 ×Vn — above threshold | Effective threshold 1.1250 A at 43.30 V |  |  |  | 43.301@0.0 | 43.301@-120.0 | 43.301@120.0 |  | 1.1813@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Characteristic runs from here
51V | Voltage-dependent overcurrent | Quick CMC | points | 4 | V = 0.75 ×Vn — below threshold | Effective threshold 1.1250 A at 43.30 V |  |  |  | 43.301@0.0 | 43.301@-120.0 | 43.301@120.0 |  | 1.0687@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
51V | Voltage-dependent overcurrent | Quick CMC | points | 5 | V = 0.5 ×Vn — above threshold | Effective threshold 750.0 mA at 28.87 V |  |  |  | 28.868@0.0 | 28.868@-120.0 | 28.868@120.0 |  | 0.7875@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Characteristic runs from here
51V | Voltage-dependent overcurrent | Quick CMC | points | 6 | V = 0.5 ×Vn — below threshold | Effective threshold 750.0 mA at 28.87 V |  |  |  | 28.868@0.0 | 28.868@-120.0 | 28.868@120.0 |  | 0.7125@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
51V | Voltage-dependent overcurrent | Quick CMC | points | 7 | V = 0.25 ×Vn — above threshold | Effective threshold 375.0 mA at 14.43 V |  |  |  | 14.434@0.0 | 14.434@-120.0 | 14.434@120.0 |  | 0.3938@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Characteristic runs from here
51V | Voltage-dependent overcurrent | Quick CMC | points | 8 | V = 0.25 ×Vn — below threshold | Effective threshold 375.0 mA at 14.43 V |  |  |  | 14.434@0.0 | 14.434@-120.0 | 14.434@120.0 |  | 0.3562@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
79 | Auto-reclose | State Sequencer | sequence | 1 | Permanent — prefault load | Healthy circuit held long enough for the scheme to be ready | 1 | 1/5 | 2 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.4500@-25.8 | 0.4500@-145.8 | 0.4500@94.2 | 50 | yes | READY | Cycle counter at zero
79 | Auto-reclose | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | Fault still present on every reclose, 6 × In applied | 1 | 2/5 | 0.06 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 6.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | TRIP, RECLOSE STARTED | Trip in 0.060 s
79 | Auto-reclose | State Sequencer | sequence | 3 | Permanent — dead time 1 | Breaker open, line dead. Dead time 1 is 0.400 s. | 1 | 3/5 | 0.4 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RECLOSE AT 0.400 s | Close command at the end of this state, not before
79 | Auto-reclose | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | Fault still present on every reclose, 6 × In applied | 1 | 4/5 | 0.06 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 6.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | TRIP, CYCLE 2 | Trip in 0.060 s
79 | Auto-reclose | State Sequencer | sequence | 5 | Permanent — final trip | No cycles left after 2. Breaker open, no further close. | 1 | 5/5 | 3 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | FINAL TRIP | The scheme must stay blocked until reset
79 | Auto-reclose | State Sequencer | sequence | 6 | Transient — prefault load | Healthy circuit, scheme ready | 2 | 1/5 | 2 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.4500@-25.8 | 0.4500@-145.8 | 0.4500@94.2 | 50 | yes | READY | Counter at zero
79 | Auto-reclose | State Sequencer | sequence | 7 | Transient — fault | One fault, cleared by the trip and gone before the reclose | 2 | 2/5 | 0.06 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 6.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | TRIP, RECLOSE STARTED | Trip in 0.060 s
79 | Auto-reclose | State Sequencer | sequence | 8 | Transient — dead time 1 | Breaker open. The fault is removed during this state. | 2 | 3/5 | 0.4 | 0.000@0.0 | 0.000@-120.0 | 0.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RECLOSE AT 0.400 s | Close at the end of the dead time
79 | Auto-reclose | State Sequencer | sequence | 9 | Transient — reclaim | Load restored and held for the full 15.00 s reclaim time | 2 | 4/5 | 15 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.4500@-25.8 | 0.4500@-145.8 | 0.4500@94.2 | 50 | yes | NO TRIP | A second fault inside this window goes to the next cycle
79 | Auto-reclose | State Sequencer | sequence | 10 | Transient — reset confirmed | Reclaim expired, counter back to zero | 2 | 5/5 | 3 | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.4500@-25.8 | 0.4500@-145.8 | 0.4500@94.2 | 50 | yes | RESET | A fault now counts as cycle 1 again
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above | 105% of the detector setting, no initiate |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.1050@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | DETECTOR PICKED UP | Flag only, no trip without initiate
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below | 95% of the detector setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0950@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | NO PICKUP | Detector must drop out
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | Initiate asserted with current held and never removed |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.150 s | Stage 1
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing | Same state, second stage |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.3000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 0.250 s | Stage 2 — trips the busbar zone
50BF | Circuit-breaker failure | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | Initiate asserted, then current removed inside stage 1 |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@-72.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | NO TRIP | Proves the detector reset stops the scheme
74TC | Trip circuit supervision | — | binary / DC | 1 | Healthy circuit | Trip circuit intact, breaker closed | [11 empty] | yes | NO ALARM | Both binary inputs energised
74TC | Trip circuit supervision | — | binary / DC | 2 | Trip coil open | Open the trip-coil circuit at the terminal block | [11 empty] | yes | ALARM | After 2.000 s
74TC | Trip circuit supervision | — | binary / DC | 3 | Trip supply lost | Remove the DC supply to the trip circuit | [11 empty] | yes | ALARM | After 2.000 s
74TC | Trip circuit supervision | — | binary / DC | 4 | Breaker open | Breaker open with the circuit intact | [11 empty] | yes | NO ALARM | The scheme must not alarm on a normally open breaker — this is the point that catches a one-input arrangement wired as if it were two
25 | Synchrocheck | Synchronizer | points | 1 | In synchronism | All three differences well inside their limits |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz
25 | Synchrocheck | Synchronizer | points | 2 | Angle inside limit | Angle at 80% of the setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@12.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | CLOSE RELEASED | Δθ 12.0°
25 | Synchrocheck | Synchronizer | points | 3 | Angle outside limit | Angle at 120% of the setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@18.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | BLOCKED | Δθ 18.0°
25 | Synchrocheck | Synchronizer | points | 4 | Voltage difference outside | Angle matched, magnitude offset past ΔV |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 50.535@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | BLOCKED | ΔV 7.20 V
25 | Synchrocheck | Synchronizer | points | 5 | Slip outside limit | Line output run off frequency so the angle rotates |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 57.735@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | BLOCKED | Δf 0.096 Hz
25 | Synchrocheck | Synchronizer | points | 6 | Dead line, live bus | Line collapsed below the dead threshold — the normal reclose case |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check
27 | Undervoltage | Voltage | pickup+time | 1 | Threshold — below | 95% of setting |  |  |  | 43.879@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate after 3.000 s
27 | Undervoltage | Voltage | pickup+time | 2 | Threshold — above | 105% of setting |  |  |  | 48.497@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
27 | Undervoltage | Voltage | pickup+time | 3 | Timing at 0.5× threshold | Step from nominal to the test level |  |  |  | 23.094@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 3.000 s | Definite time
27 | Undervoltage | Voltage | pickup+time | 4 | Below minimum operating voltage | Proves the function blocks rather than operating on a dead feeder |  |  |  | 4.000@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | BLOCKED | Function inhibited
59 | Overvoltage | Voltage | pickup+time | 1 | Threshold — above | 105% of setting |  |  |  | 66.684@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate after 1.500 s
59 | Overvoltage | Voltage | pickup+time | 2 | Threshold — below | 95% of setting |  |  |  | 60.333@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
59 | Overvoltage | Voltage | pickup+time | 3 | Timing at 1.25× threshold | Step from nominal to the test level |  |  |  | 79.386@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | 1.500 s | Definite time
47 | Voltage unbalance / phase rotation | Quick CMC | points | 1 | Threshold — above | Balanced set in reverse rotation — every volt applied is negative sequence |  |  |  | 6.351@0.0 | 6.351@120.0 | 6.351@-120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate after 3.000 s
47 | Voltage unbalance / phase rotation | Quick CMC | points | 2 | Threshold — below | Balanced set in reverse rotation — every volt applied is negative sequence |  |  |  | 5.196@0.0 | 5.196@120.0 | 5.196@-120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
47 | Voltage unbalance / phase rotation | Quick CMC | points | 3 | Full phase reversal | Nominal set with L2 and L3 exchanged |  |  |  | 57.735@0.0 | 57.735@120.0 | 57.735@-120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | V2 = 57.74 V
81 | Under / over frequency | Quick CMC | points | 1 | Threshold — past | 0.050 Hz beyond the setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 48.95 | yes | OPERATE | Operate after 0.500 s
81 | Under / over frequency | Quick CMC | points | 2 | Threshold — short of | 0.050 Hz on the healthy side |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 49.05 | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 3 | Timing | Step from 50.0 Hz straight to 48.950 Hz |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 48.95 | yes | 0.500 s | Definite time
81 | Under / over frequency | Quick CMC | points | 4 | Below minimum voltage | Frequency past the setting but voltage under the 30 V level |  |  |  | 24.000@0.0 | 24.000@-120.0 | 24.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 48.95 | yes | BLOCKED | Function inhibited
81R | Rate of frequency change | Ramping | ramp | 1 | Rate above threshold | Ramp 50.00 → 47.00 Hz at 1.200 Hz/s · 2.500 s of travel |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate after 0.200 s of sustained rate
81R | Rate of frequency change | Ramping | ramp | 2 | Rate below threshold | Ramp 50.00 → 47.00 Hz at 0.800 Hz/s · 3.750 s of travel |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | RESTRAIN | No operation
81R | Rate of frequency change | Ramping | ramp | 3 | Well above threshold | Ramp 50.00 → 47.00 Hz at 3.000 Hz/s · 1.000 s of travel |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 50 | yes | OPERATE | Operate after 0.200 s of sustained rate
32 | Directional power | Quick CMC | points | 1 | Above threshold | 110% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0397@0.0 | 0.0397@-120.0 | 0.0397@120.0 | 50 | yes | OPERATE | Balanced 3φ · 550.0 kW primary
32 | Directional power | Quick CMC | points | 2 | Below threshold | 90% of setting |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0325@0.0 | 0.0325@-120.0 | 0.0325@120.0 | 50 | yes | RESTRAIN | Balanced 3φ · 450.0 kW primary
32 | Directional power | Quick CMC | points | 3 | Timing at 2× threshold | Definite time |  |  |  | 57.735@0.0 | 57.735@-120.0 | 57.735@120.0 |  | 0.0722@0.0 | 0.0722@-120.0 | 0.0722@120.0 | 50 | yes | 2.000 s | Balanced 3φ · 1000.0 kW primary

## Channels
Function | Description | Group | TU module | Drive as | # | Test step | Run | State | State label | Dur s | Channel | Magnitude | Unit | Angle deg | Hz | Note | Expected | Expected — detail | Verdict
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 1 | Forward — full component |  |  |  |  | I aux | 0.06 | A | 0 | 50 | core-balance CT input (3I0) | OPERATE | Component 60.0 mA against a 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 2 | Reverse |  |  |  |  | I aux | 0.06 | A | 180 | 50 | core-balance CT input (3I0) | RESTRAIN | No operation in the reverse half-plane | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 3 | Sector edge, leading side (inside) |  |  |  |  | I aux | 0.06 | A | 67.52 | 50 | core-balance CT input (3I0) | OPERATE | Component still above the 15.0 mA threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 4 | Sector edge, leading side (outside) |  |  |  |  | I aux | 0.06 | A | 83.52 | 50 | core-balance CT input (3I0) | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 5 | Sector edge, lagging side (inside) |  |  |  |  | I aux | 0.06 | A | -67.52 | 50 | core-balance CT input (3I0) | OPERATE | Component still above threshold | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 6 | Sector edge, lagging side (outside) |  |  |  |  | I aux | 0.06 | A | -83.52 | 50 | core-balance CT input (3I0) | RESTRAIN | Component has fallen under the threshold | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 7 | Component — above threshold |  |  |  |  | I aux | 0.018 | A | 0 | 50 | core-balance CT input (3I0) | OPERATE | Operate after 1.000 s | op
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 8 | Component — below threshold |  |  |  |  | I aux | 0.012 | A | 0 | 50 | core-balance CT input (3I0) | RESTRAIN | No operation | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | V L1 | 48.497 | V | 0 | 50 |  | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | V L2 | 62.865 | V | -127.31 | 50 |  | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | V L3 | 62.865 | V | 127.31 | 50 |  | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | V 4 | 16 | V | 180 | 50 | displacement voltage 3V0 — broken delta | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 9 | Displacement voltage withdrawn |  |  |  |  | I aux | 0.06 | A | 0 | 50 | core-balance CT input (3I0) | BLOCKED | The function has no reference to measure against | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | BLOCKED | Magnitude supervision holds it off | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | BLOCKED | Magnitude supervision holds it off | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | BLOCKED | Magnitude supervision holds it off | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage 3V0 — broken delta | BLOCKED | Magnitude supervision holds it off | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | BLOCKED | Magnitude supervision holds it off | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | BLOCKED | Magnitude supervision holds it off | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | BLOCKED | Magnitude supervision holds it off | no
67Ns | Sensitive directional ground fault | Ground fault | Quick CMC | points | 10 | Residual current below threshold |  |  |  |  | I aux | 0.008 | A | 0 | 50 | core-balance CT input (3I0) | BLOCKED | Magnitude supervision holds it off | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L1 | 45.033 | V | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L2 | 65.023 | V | -129.74 | 50 |  | OPERATE | Operate after 3.000 s | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L3 | 65.023 | V | 129.74 | 50 |  | OPERATE | Operate after 3.000 s | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V 4 | 22 | V | 180 | 50 | displacement voltage | OPERATE | Operate after 3.000 s | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L1 | 47.343 | V | 0 | 50 |  | RESTRAIN | No operation | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L2 | 63.571 | V | -128.14 | 50 |  | RESTRAIN | No operation | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L3 | 63.571 | V | 128.14 | 50 |  | RESTRAIN | No operation | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V 4 | 18 | V | 180 | 50 | displacement voltage | RESTRAIN | No operation | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
59N | Displacement voltage | Ground fault | Quick CMC | points | 3 | Reset check |  |  |  |  | V L1 | 46.985 | V | 0 | 50 |  | RESETS | Approach this one from above, having already picked up | nu
59N | Displacement voltage | Ground fault | Quick CMC | points | 3 | Reset check |  |  |  |  | V L2 | 63.793 | V | -128.39 | 50 |  | RESETS | Approach this one from above, having already picked up | nu
59N | Displacement voltage | Ground fault | Quick CMC | points | 3 | Reset check |  |  |  |  | V L3 | 63.793 | V | 128.39 | 50 |  | RESETS | Approach this one from above, having already picked up | nu
59N | Displacement voltage | Ground fault | Quick CMC | points | 3 | Reset check |  |  |  |  | V 4 | 18.62 | V | 180 | 50 | displacement voltage | RESETS | Approach this one from above, having already picked up | nu
59N | Displacement voltage | Ground fault | Quick CMC | points | 3 | Reset check |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESETS | Approach this one from above, having already picked up | nu
59N | Displacement voltage | Ground fault | Quick CMC | points | 3 | Reset check |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESETS | Approach this one from above, having already picked up | nu
59N | Displacement voltage | Ground fault | Quick CMC | points | 3 | Reset check |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESETS | Approach this one from above, having already picked up | nu
59N | Displacement voltage | Ground fault | Quick CMC | points | 4 | Fault at 25% displacement |  |  |  |  | V L1 | 43.301 | V | 0 | 50 |  | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 4 | Fault at 25% displacement |  |  |  |  | V L2 | 66.144 | V | -130.89 | 50 |  | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 4 | Fault at 25% displacement |  |  |  |  | V L3 | 66.144 | V | 130.89 | 50 |  | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 4 | Fault at 25% displacement |  |  |  |  | V 4 | 25 | V | 180 | 50 | displacement voltage | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 4 | Fault at 25% displacement |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 4 | Fault at 25% displacement |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 4 | Fault at 25% displacement |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 43.3 / 66.1 / 66.1 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 5 | Fault at 50% displacement |  |  |  |  | V L1 | 28.868 | V | 0 | 50 |  | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 5 | Fault at 50% displacement |  |  |  |  | V L2 | 76.376 | V | -139.11 | 50 |  | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 5 | Fault at 50% displacement |  |  |  |  | V L3 | 76.376 | V | 139.11 | 50 |  | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 5 | Fault at 50% displacement |  |  |  |  | V 4 | 50 | V | 180 | 50 | displacement voltage | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 5 | Fault at 50% displacement |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 5 | Fault at 50% displacement |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 5 | Fault at 50% displacement |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 28.9 / 76.4 / 76.4 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 6 | Fault at 100% displacement |  |  |  |  | V L1 | 0 | V | 0 | 50 | faulted phase, collapsed | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 6 | Fault at 100% displacement |  |  |  |  | V L2 | 100 | V | -150 | 50 |  | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 6 | Fault at 100% displacement |  |  |  |  | V L3 | 100 | V | 150 | 50 |  | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 6 | Fault at 100% displacement |  |  |  |  | V 4 | 100 | V | 180 | 50 | displacement voltage | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 6 | Fault at 100% displacement |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 6 | Fault at 100% displacement |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V | op
59N | Displacement voltage | Ground fault | Quick CMC | points | 6 | Fault at 100% displacement |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Phase voltages 0.0 / 100.0 / 100.0 V | op
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.100 s | op
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.100 s | op
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L1 | 2.625 | A | -72 | 50 |  | OPERATE | Operate within 0.100 s | op
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L1 | 2.375 | A | -72 | 50 |  | RESTRAIN | No operation | no
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 5 | A | -72 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-1 | Overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.100 s | op
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.100 s | op
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L1 | 8.4 | A | -72 | 50 |  | OPERATE | Operate within 0.100 s | op
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L1 | 7.6 | A | -72 | 50 |  | RESTRAIN | No operation | no
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 16 | A | -72 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50-2 | Overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L1 | 1.26 | A | -72 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L1 | 1.14 | A | -72 | 50 |  | RESTRAIN | No operation | no
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 2.4 | A | -72 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | I L1 | 3.6 | A | -72 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | I L1 | 6 | A | -72 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.594 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.594 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.594 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | I L1 | 12 | A | -72 | 50 |  | 0.594 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.594 s | From the characteristic equation | nu
51 | Overcurrent inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.594 s | From the characteristic equation | nu
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I aux | 0.42 | A | -72 | 50 | core-balance CT input — the device measures IN here | OPERATE | Operate within 0.100 s | op
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I aux | 0.38 | A | -72 | 50 | core-balance CT input — the device measures IN here | RESTRAIN | No operation | no
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-1 | Ground overcurrent stage 1 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I aux | 0.8 | A | -72 | 50 | core-balance CT input — the device measures IN here | 0.100 s | Measured from the current step to the trip | nu
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — above |  |  |  |  | I aux | 2.1 | A | -72 | 50 | core-balance CT input — the device measures IN here | OPERATE | Operate within 0.100 s | op
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — below |  |  |  |  | I aux | 1.9 | A | -72 | 50 | core-balance CT input — the device measures IN here | RESTRAIN | No operation | no
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
50N-2 | Ground overcurrent stage 2 | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× threshold |  |  |  |  | I aux | 4 | A | -72 | 50 | core-balance CT input — the device measures IN here | 0.100 s | Measured from the current step to the trip | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Long operate time — let the characteristic run out | op
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I aux | 0.2625 | A | -72 | 50 | core-balance CT input — the device measures IN here | OPERATE | Long operate time — let the characteristic run out | op
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I aux | 0.2375 | A | -72 | 50 | core-balance CT input — the device measures IN here | RESTRAIN | No operation | no
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.006 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.006 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 2.006 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I aux | 0.5 | A | -72 | 50 | core-balance CT input — the device measures IN here | 2.006 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 1.260 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 1.260 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 1.260 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× threshold |  |  |  |  | I aux | 0.75 | A | -72 | 50 | core-balance CT input — the device measures IN here | 1.260 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.856 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.856 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.856 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× threshold |  |  |  |  | I aux | 1.25 | A | -72 | 50 | core-balance CT input — the device measures IN here | 0.856 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.594 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.594 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.594 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 0.594 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.594 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.594 s | From the characteristic equation | nu
51N | Ground inverse time | Overcurrent | Overcurrent | characteristic | 6 | Timing at 10× threshold |  |  |  |  | I aux | 2.5 | A | -72 | 50 | core-balance CT input — the device measures IN here | 0.594 s | From the characteristic equation | nu
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate within 0.100 s | op
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate within 0.100 s | op
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L1 | 0.945 | A | -72 | 50 |  | OPERATE | Operate within 0.100 s | op
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate within 0.100 s | op
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L1 | 0.855 | A | -72 | 50 |  | RESTRAIN | No operation | no
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 1.8 | A | -72 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
46 | Unbalanced load | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.100 s | Measured from the current step to the trip | nu
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 1 | Harmonic above threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | Overcurrent stages held off | no
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 1 | Harmonic above threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Overcurrent stages held off | no
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 1 | Harmonic above threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Overcurrent stages held off | no
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 1 | Harmonic above threshold |  |  |  |  | I L1 | 3 | A | 0 | 50 | fundamental | BLOCKED | Overcurrent stages held off | no
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 1 | Harmonic above threshold |  |  |  |  | I L1 | 0.5175 | A | 0 | 100 | 2nd harmonic — superimposed on the same output | BLOCKED | Overcurrent stages held off | no
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 2 | Harmonic below threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | The overcurrent stage is released and trips | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 2 | Harmonic below threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | The overcurrent stage is released and trips | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 2 | Harmonic below threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | The overcurrent stage is released and trips | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 2 | Harmonic below threshold |  |  |  |  | I L1 | 3 | A | 0 | 50 | fundamental | OPERATE | The overcurrent stage is released and trips | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 2 | Harmonic below threshold |  |  |  |  | I L1 | 0.3825 | A | 0 | 100 | 2nd harmonic — superimposed on the same output | OPERATE | The overcurrent stage is released and trips | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 3 | No harmonic |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | This is the case an ordinary overcurrent test produces | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 3 | No harmonic |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | This is the case an ordinary overcurrent test produces | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 3 | No harmonic |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | This is the case an ordinary overcurrent test produces | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 3 | No harmonic |  |  |  |  | I L1 | 3 | A | 0 | 50 | fundamental | OPERATE | This is the case an ordinary overcurrent test produces | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 3 | No harmonic |  |  |  |  | I L1 | 0 | A | 0 | 100 | 2nd harmonic — superimposed on the same output | OPERATE | This is the case an ordinary overcurrent test produces | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 4 | Above the upper limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Blocking is abandoned above the upper limit — a real fault does not wait for the harmonic to clear | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 4 | Above the upper limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Blocking is abandoned above the upper limit — a real fault does not wait for the harmonic to clear | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 4 | Above the upper limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Blocking is abandoned above the upper limit — a real fault does not wait for the harmonic to clear | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 4 | Above the upper limit |  |  |  |  | I L1 | 9.6 | A | 0 | 50 | fundamental, past the upper limit | OPERATE | Blocking is abandoned above the upper limit — a real fault does not wait for the harmonic to clear | op
Inrush | 2nd harmonic inrush restraint | Overcurrent | Harmonics | points | 4 | Above the upper limit |  |  |  |  | I L1 | 1.656 | A | 0 | 100 | 2nd harmonic | OPERATE | Blocking is abandoned above the upper limit — a real fault does not wait for the harmonic to clear | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Z1 reach — inside |  |  |  |  | V L1 | 57.735 | V | 90 | 50 | healthy phase, at nominal | ZONE 1 | Operate after 0.000 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Z1 reach — inside |  |  |  |  | V L2 | 28.951 | V | -85.64 | 50 |  | ZONE 1 | Operate after 0.000 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Z1 reach — inside |  |  |  |  | V L3 | 28.951 | V | -94.36 | 50 |  | ZONE 1 | Operate after 0.000 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Z1 reach — inside |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | ZONE 1 | Operate after 0.000 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Z1 reach — inside |  |  |  |  | I L2 | 1 | A | -72 | 50 |  | ZONE 1 | Operate after 0.000 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 1 | Z1 reach — inside |  |  |  |  | I L3 | 1 | A | 108 | 50 |  | ZONE 1 | Operate after 0.000 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Z1 reach — outside |  |  |  |  | V L1 | 57.735 | V | 90 | 50 | healthy phase, at nominal | NOT ZONE 1 | Picked up by Z2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Z1 reach — outside |  |  |  |  | V L2 | 28.993 | V | -84.67 | 50 |  | NOT ZONE 1 | Picked up by Z2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Z1 reach — outside |  |  |  |  | V L3 | 28.993 | V | -95.33 | 50 |  | NOT ZONE 1 | Picked up by Z2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Z1 reach — outside |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | NOT ZONE 1 | Picked up by Z2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Z1 reach — outside |  |  |  |  | I L2 | 1 | A | -72 | 50 |  | NOT ZONE 1 | Picked up by Z2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 2 | Z1 reach — outside |  |  |  |  | I L3 | 1 | A | 108 | 50 |  | NOT ZONE 1 | Picked up by Z2 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Z2 reach — inside |  |  |  |  | V L1 | 57.735 | V | 90 | 50 | healthy phase, at nominal | ZONE 2 | Operate after 0.300 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Z2 reach — inside |  |  |  |  | V L2 | 29.035 | V | -83.85 | 50 |  | ZONE 2 | Operate after 0.300 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Z2 reach — inside |  |  |  |  | V L3 | 29.035 | V | -96.15 | 50 |  | ZONE 2 | Operate after 0.300 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Z2 reach — inside |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | ZONE 2 | Operate after 0.300 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Z2 reach — inside |  |  |  |  | I L2 | 1 | A | -72 | 50 |  | ZONE 2 | Operate after 0.300 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 3 | Z2 reach — inside |  |  |  |  | I L3 | 1 | A | 108 | 50 |  | ZONE 2 | Operate after 0.300 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Z2 reach — outside |  |  |  |  | V L1 | 57.735 | V | 90 | 50 | healthy phase, at nominal | NOT ZONE 2 | Picked up by Z3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Z2 reach — outside |  |  |  |  | V L2 | 29.117 | V | -82.5 | 50 |  | NOT ZONE 2 | Picked up by Z3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Z2 reach — outside |  |  |  |  | V L3 | 29.117 | V | -97.5 | 50 |  | NOT ZONE 2 | Picked up by Z3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Z2 reach — outside |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | NOT ZONE 2 | Picked up by Z3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Z2 reach — outside |  |  |  |  | I L2 | 1 | A | -72 | 50 |  | NOT ZONE 2 | Picked up by Z3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 4 | Z2 reach — outside |  |  |  |  | I L3 | 1 | A | 108 | 50 |  | NOT ZONE 2 | Picked up by Z3 instead | no
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Z3 reach — inside |  |  |  |  | V L1 | 57.735 | V | 90 | 50 | healthy phase, at nominal | ZONE 3 | Operate after 0.900 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Z3 reach — inside |  |  |  |  | V L2 | 29.329 | V | -79.82 | 50 |  | ZONE 3 | Operate after 0.900 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Z3 reach — inside |  |  |  |  | V L3 | 29.329 | V | -100.18 | 50 |  | ZONE 3 | Operate after 0.900 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Z3 reach — inside |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | ZONE 3 | Operate after 0.900 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Z3 reach — inside |  |  |  |  | I L2 | 1 | A | -72 | 50 |  | ZONE 3 | Operate after 0.900 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 5 | Z3 reach — inside |  |  |  |  | I L3 | 1 | A | 108 | 50 |  | ZONE 3 | Operate after 0.900 s | op
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Z3 reach — outside |  |  |  |  | V L1 | 57.735 | V | 90 | 50 | healthy phase, at nominal | NOT ZONE 3 | No zone sees it | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Z3 reach — outside |  |  |  |  | V L2 | 29.555 | V | -77.62 | 50 |  | NOT ZONE 3 | No zone sees it | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Z3 reach — outside |  |  |  |  | V L3 | 29.555 | V | -102.38 | 50 |  | NOT ZONE 3 | No zone sees it | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Z3 reach — outside |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | NOT ZONE 3 | No zone sees it | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Z3 reach — outside |  |  |  |  | I L2 | 1 | A | -72 | 50 |  | NOT ZONE 3 | No zone sees it | no
21 | Distance zones | Distance | Advanced Distance | shots | 6 | Z3 reach — outside |  |  |  |  | I L3 | 1 | A | 108 | 50 |  | NOT ZONE 3 | No zone sees it | no
FLOC | Fault locator | Distance | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | V L1 | 0.496 | V | 0 | 50 | faulted phase | 1.20 km | Accept 0.60 to 1.80 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 1.20 km | Accept 0.60 to 1.80 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 1.20 km | Accept 0.60 to 1.80 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | I L1 | 1 | A | -69.55 | 50 |  | 1.20 km | Accept 0.60 to 1.80 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 1.20 km | Accept 0.60 to 1.80 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 1 | Fault at 10% of line |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 1.20 km | Accept 0.60 to 1.80 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | V L1 | 1.239 | V | 0 | 50 | faulted phase | 3.00 km | Accept 2.40 to 3.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 3.00 km | Accept 2.40 to 3.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 3.00 km | Accept 2.40 to 3.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | I L1 | 1 | A | -69.55 | 50 |  | 3.00 km | Accept 2.40 to 3.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 3.00 km | Accept 2.40 to 3.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 2 | Fault at 25% of line |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 3.00 km | Accept 2.40 to 3.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | V L1 | 2.479 | V | 0 | 50 | faulted phase | 6.00 km | Accept 5.40 to 6.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 6.00 km | Accept 5.40 to 6.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 6.00 km | Accept 5.40 to 6.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | I L1 | 1 | A | -69.55 | 50 |  | 6.00 km | Accept 5.40 to 6.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 6.00 km | Accept 5.40 to 6.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 3 | Fault at 50% of line |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 6.00 km | Accept 5.40 to 6.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | V L1 | 3.718 | V | 0 | 50 | faulted phase | 9.00 km | Accept 8.40 to 9.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 9.00 km | Accept 8.40 to 9.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 9.00 km | Accept 8.40 to 9.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | I L1 | 1 | A | -69.55 | 50 |  | 9.00 km | Accept 8.40 to 9.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 9.00 km | Accept 8.40 to 9.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 4 | Fault at 75% of line |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 9.00 km | Accept 8.40 to 9.60 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | V L1 | 4.461 | V | 0 | 50 | faulted phase | 10.80 km | Accept 10.20 to 11.40 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 10.80 km | Accept 10.20 to 11.40 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 10.80 km | Accept 10.20 to 11.40 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | I L1 | 1 | A | -69.55 | 50 |  | 10.80 km | Accept 10.20 to 11.40 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 10.80 km | Accept 10.20 to 11.40 km | nu
FLOC | Fault locator | Distance | Advanced Distance | shots | 5 | Fault at 90% of line |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 10.80 km | Accept 10.20 to 11.40 km | nu
67 | Directional overcurrent | Directional | Ramping | points | 1 | Forward — maximum torque |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 1 | Forward — maximum torque |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 1 | Forward — maximum torque |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 1 | Forward — maximum torque |  |  |  |  | I L1 | 2.4 | A | -45 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 1 | Forward — maximum torque |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 1 | Forward — maximum torque |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 2 | Reverse — maximum torque |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 2 | Reverse — maximum torque |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 2 | Reverse — maximum torque |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 2 | Reverse — maximum torque |  |  |  |  | I L1 | 2.4 | A | 135 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 2 | Reverse — maximum torque |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 2 | Reverse — maximum torque |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 3 | Boundary, leading (inside) |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 3 | Boundary, leading (inside) |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 3 | Boundary, leading (inside) |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 3 | Boundary, leading (inside) |  |  |  |  | I L1 | 2.4 | A | 40 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 3 | Boundary, leading (inside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 3 | Boundary, leading (inside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 4 | Boundary, leading (outside) |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 4 | Boundary, leading (outside) |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 4 | Boundary, leading (outside) |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 4 | Boundary, leading (outside) |  |  |  |  | I L1 | 2.4 | A | 50 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 4 | Boundary, leading (outside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 4 | Boundary, leading (outside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 5 | Boundary, lagging (inside) |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 5 | Boundary, lagging (inside) |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 5 | Boundary, lagging (inside) |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 5 | Boundary, lagging (inside) |  |  |  |  | I L1 | 2.4 | A | -130 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 5 | Boundary, lagging (inside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 5 | Boundary, lagging (inside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | FORWARD | Current held at 2.0× threshold | op
67 | Directional overcurrent | Directional | Ramping | points | 6 | Boundary, lagging (outside) |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 6 | Boundary, lagging (outside) |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 6 | Boundary, lagging (outside) |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 6 | Boundary, lagging (outside) |  |  |  |  | I L1 | 2.4 | A | -140 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 6 | Boundary, lagging (outside) |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
67 | Directional overcurrent | Directional | Ramping | points | 6 | Boundary, lagging (outside) |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | REVERSE | Current held at 2.0× threshold | no
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× k·In |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 2.83 min | Alarm at 2.55 min | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× k·In |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.83 min | Alarm at 2.55 min | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× k·In |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.83 min | Alarm at 2.55 min | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× k·In |  |  |  |  | I L1 | 1.65 | A | -26 | 50 |  | 2.83 min | Alarm at 2.55 min | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× k·In |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 2.83 min | Alarm at 2.55 min | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× k·In |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 2.83 min | Alarm at 2.55 min | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× k·In |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 73.69 s | Alarm at 66.32 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× k·In |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 73.69 s | Alarm at 66.32 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× k·In |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 73.69 s | Alarm at 66.32 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× k·In |  |  |  |  | I L1 | 2.2 | A | -26 | 50 |  | 73.69 s | Alarm at 66.32 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× k·In |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 73.69 s | Alarm at 66.32 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× k·In |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 73.69 s | Alarm at 66.32 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× k·In |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 28.17 s | Alarm at 25.35 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× k·In |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 28.17 s | Alarm at 25.35 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× k·In |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 28.17 s | Alarm at 25.35 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× k·In |  |  |  |  | I L1 | 3.3 | A | -26 | 50 |  | 28.17 s | Alarm at 25.35 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× k·In |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 28.17 s | Alarm at 25.35 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× k·In |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 28.17 s | Alarm at 25.35 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× k·In |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 9.463 s | Alarm at 8.516 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× k·In |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 9.463 s | Alarm at 8.516 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× k·In |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 9.463 s | Alarm at 8.516 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× k·In |  |  |  |  | I L1 | 5.5 | A | -26 | 50 |  | 9.463 s | Alarm at 8.516 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× k·In |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 9.463 s | Alarm at 8.516 s | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× k·In |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 9.463 s | Alarm at 8.516 s | nu
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate after 3.000 s | op
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate after 3.000 s | op
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — below |  |  |  |  | I L1 | 0.19 | A | -26 | 50 |  | OPERATE | Operate after 3.000 s | op
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — below |  |  |  |  | I L2 | 0.19 | A | -146 | 50 |  | OPERATE | Operate after 3.000 s | op
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 1 | Threshold — below |  |  |  |  | I L3 | 0.19 | A | 94 | 50 |  | OPERATE | Operate after 3.000 s | op
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — above |  |  |  |  | I L1 | 0.21 | A | -26 | 50 |  | RESTRAIN | No operation | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — above |  |  |  |  | I L2 | 0.21 | A | -146 | 50 |  | RESTRAIN | No operation | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 2 | Threshold — above |  |  |  |  | I L3 | 0.21 | A | 94 | 50 |  | RESTRAIN | No operation | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 3.000 s | Definite time | nu
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 3.000 s | Definite time | nu
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 3.000 s | Definite time | nu
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half threshold |  |  |  |  | I L1 | 0.1 | A | -26 | 50 |  | 3.000 s | Definite time | nu
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half threshold |  |  |  |  | I L2 | 0.1 | A | -146 | 50 |  | 3.000 s | Definite time | nu
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 3 | Timing at half threshold |  |  |  |  | I L3 | 0.1 | A | 94 | 50 |  | 3.000 s | Definite time | nu
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 4 | Open circuit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | An open breaker must not read as lost load | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 4 | Open circuit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | An open breaker must not read as lost load | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 4 | Open circuit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | An open breaker must not read as lost load | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 4 | Open circuit |  |  |  |  | I L1 | 0.015 | A | -26 | 50 |  | BLOCKED | An open breaker must not read as lost load | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 4 | Open circuit |  |  |  |  | I L2 | 0.015 | A | -146 | 50 |  | BLOCKED | An open breaker must not read as lost load | no
37 | Undercurrent | Overcurrent | Overcurrent | pickup+time | 4 | Open circuit |  |  |  |  | I L3 | 0.015 | A | 94 | 50 |  | BLOCKED | An open breaker must not read as lost load | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 1 | V = 1 ×Vn — above threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 1 | V = 1 ×Vn — above threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 1 | V = 1 ×Vn — above threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 1 | V = 1 ×Vn — above threshold |  |  |  |  | I L1 | 1.575 | A | -72 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 1 | V = 1 ×Vn — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 1 | V = 1 ×Vn — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 2 | V = 1 ×Vn — below threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 2 | V = 1 ×Vn — below threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 2 | V = 1 ×Vn — below threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 2 | V = 1 ×Vn — below threshold |  |  |  |  | I L1 | 1.425 | A | -72 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 2 | V = 1 ×Vn — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 2 | V = 1 ×Vn — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 3 | V = 0.75 ×Vn — above threshold |  |  |  |  | V L1 | 43.301 | V | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 3 | V = 0.75 ×Vn — above threshold |  |  |  |  | V L2 | 43.301 | V | -120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 3 | V = 0.75 ×Vn — above threshold |  |  |  |  | V L3 | 43.301 | V | 120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 3 | V = 0.75 ×Vn — above threshold |  |  |  |  | I L1 | 1.1813 | A | -72 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 3 | V = 0.75 ×Vn — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 3 | V = 0.75 ×Vn — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 4 | V = 0.75 ×Vn — below threshold |  |  |  |  | V L1 | 43.301 | V | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 4 | V = 0.75 ×Vn — below threshold |  |  |  |  | V L2 | 43.301 | V | -120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 4 | V = 0.75 ×Vn — below threshold |  |  |  |  | V L3 | 43.301 | V | 120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 4 | V = 0.75 ×Vn — below threshold |  |  |  |  | I L1 | 1.0687 | A | -72 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 4 | V = 0.75 ×Vn — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 4 | V = 0.75 ×Vn — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 5 | V = 0.5 ×Vn — above threshold |  |  |  |  | V L1 | 28.868 | V | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 5 | V = 0.5 ×Vn — above threshold |  |  |  |  | V L2 | 28.868 | V | -120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 5 | V = 0.5 ×Vn — above threshold |  |  |  |  | V L3 | 28.868 | V | 120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 5 | V = 0.5 ×Vn — above threshold |  |  |  |  | I L1 | 0.7875 | A | -72 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 5 | V = 0.5 ×Vn — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 5 | V = 0.5 ×Vn — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 6 | V = 0.5 ×Vn — below threshold |  |  |  |  | V L1 | 28.868 | V | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 6 | V = 0.5 ×Vn — below threshold |  |  |  |  | V L2 | 28.868 | V | -120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 6 | V = 0.5 ×Vn — below threshold |  |  |  |  | V L3 | 28.868 | V | 120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 6 | V = 0.5 ×Vn — below threshold |  |  |  |  | I L1 | 0.7125 | A | -72 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 6 | V = 0.5 ×Vn — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 6 | V = 0.5 ×Vn — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 7 | V = 0.25 ×Vn — above threshold |  |  |  |  | V L1 | 14.434 | V | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 7 | V = 0.25 ×Vn — above threshold |  |  |  |  | V L2 | 14.434 | V | -120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 7 | V = 0.25 ×Vn — above threshold |  |  |  |  | V L3 | 14.434 | V | 120 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 7 | V = 0.25 ×Vn — above threshold |  |  |  |  | I L1 | 0.3938 | A | -72 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 7 | V = 0.25 ×Vn — above threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 7 | V = 0.25 ×Vn — above threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Characteristic runs from here | op
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 8 | V = 0.25 ×Vn — below threshold |  |  |  |  | V L1 | 14.434 | V | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 8 | V = 0.25 ×Vn — below threshold |  |  |  |  | V L2 | 14.434 | V | -120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 8 | V = 0.25 ×Vn — below threshold |  |  |  |  | V L3 | 14.434 | V | 120 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 8 | V = 0.25 ×Vn — below threshold |  |  |  |  | I L1 | 0.3562 | A | -72 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 8 | V = 0.25 ×Vn — below threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
51V | Voltage-dependent overcurrent | Overcurrent | Quick CMC | points | 8 | V = 0.25 ×Vn — below threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | V L1 | 57.735 | V | 0 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | V L2 | 57.735 | V | -120 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | V L3 | 57.735 | V | 120 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | I L1 | 0.45 | A | -25.84 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | I L2 | 0.45 | A | -145.84 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 1 | Permanent — prefault load | 1 | 1/5 | Load | 2 | I L3 | 0.45 | A | 94.16 | 50 |  | READY | Cycle counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.06 | V L1 | 57.735 | V | 0 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.06 | V L2 | 57.735 | V | -120 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.06 | V L3 | 57.735 | V | 120 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.06 | I L1 | 6 | A | -72 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.06 | I L2 | 0 | A | 0 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 2 | Permanent — fault 1 of 2 | 1 | 2/5 | Fault 1 | 0.06 | I L3 | 0 | A | 0 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.4 | V L1 | 0 | V | 0 | 50 |  | RECLOSE AT 0.400 s | Close command at the end of this state, not before | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.4 | V L2 | 0 | V | -120 | 50 |  | RECLOSE AT 0.400 s | Close command at the end of this state, not before | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.4 | V L3 | 0 | V | 120 | 50 |  | RECLOSE AT 0.400 s | Close command at the end of this state, not before | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.4 | I L1 | 0 | A | 0 | 50 |  | RECLOSE AT 0.400 s | Close command at the end of this state, not before | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.4 | I L2 | 0 | A | 0 | 50 |  | RECLOSE AT 0.400 s | Close command at the end of this state, not before | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 3 | Permanent — dead time 1 | 1 | 3/5 | Dead 1 | 0.4 | I L3 | 0 | A | 0 | 50 |  | RECLOSE AT 0.400 s | Close command at the end of this state, not before | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.06 | V L1 | 57.735 | V | 0 | 50 |  | TRIP, CYCLE 2 | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.06 | V L2 | 57.735 | V | -120 | 50 |  | TRIP, CYCLE 2 | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.06 | V L3 | 57.735 | V | 120 | 50 |  | TRIP, CYCLE 2 | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.06 | I L1 | 6 | A | -72 | 50 |  | TRIP, CYCLE 2 | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.06 | I L2 | 0 | A | 0 | 50 |  | TRIP, CYCLE 2 | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 4 | Permanent — fault 2 of 2 | 1 | 4/5 | Fault 2 | 0.06 | I L3 | 0 | A | 0 | 50 |  | TRIP, CYCLE 2 | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 5 | Permanent — final trip | 1 | 5/5 | Final trip | 3 | V L1 | 0 | V | 0 | 50 |  | FINAL TRIP | The scheme must stay blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 5 | Permanent — final trip | 1 | 5/5 | Final trip | 3 | V L2 | 0 | V | -120 | 50 |  | FINAL TRIP | The scheme must stay blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 5 | Permanent — final trip | 1 | 5/5 | Final trip | 3 | V L3 | 0 | V | 120 | 50 |  | FINAL TRIP | The scheme must stay blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 5 | Permanent — final trip | 1 | 5/5 | Final trip | 3 | I L1 | 0 | A | 0 | 50 |  | FINAL TRIP | The scheme must stay blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 5 | Permanent — final trip | 1 | 5/5 | Final trip | 3 | I L2 | 0 | A | 0 | 50 |  | FINAL TRIP | The scheme must stay blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 5 | Permanent — final trip | 1 | 5/5 | Final trip | 3 | I L3 | 0 | A | 0 | 50 |  | FINAL TRIP | The scheme must stay blocked until reset | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | V L1 | 57.735 | V | 0 | 50 |  | READY | Counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | V L2 | 57.735 | V | -120 | 50 |  | READY | Counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | V L3 | 57.735 | V | 120 | 50 |  | READY | Counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | I L1 | 0.45 | A | -25.84 | 50 |  | READY | Counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | I L2 | 0.45 | A | -145.84 | 50 |  | READY | Counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 6 | Transient — prefault load | 2 | 1/5 | Load | 2 | I L3 | 0.45 | A | 94.16 | 50 |  | READY | Counter at zero | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.06 | V L1 | 57.735 | V | 0 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.06 | V L2 | 57.735 | V | -120 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.06 | V L3 | 57.735 | V | 120 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.06 | I L1 | 6 | A | -72 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.06 | I L2 | 0 | A | 0 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 7 | Transient — fault | 2 | 2/5 | Fault | 0.06 | I L3 | 0 | A | 0 | 50 |  | TRIP, RECLOSE STARTED | Trip in 0.060 s | op
79 | Auto-reclose | Automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.4 | V L1 | 0 | V | 0 | 50 |  | RECLOSE AT 0.400 s | Close at the end of the dead time | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.4 | V L2 | 0 | V | -120 | 50 |  | RECLOSE AT 0.400 s | Close at the end of the dead time | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.4 | V L3 | 0 | V | 120 | 50 |  | RECLOSE AT 0.400 s | Close at the end of the dead time | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.4 | I L1 | 0 | A | 0 | 50 |  | RECLOSE AT 0.400 s | Close at the end of the dead time | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.4 | I L2 | 0 | A | 0 | 50 |  | RECLOSE AT 0.400 s | Close at the end of the dead time | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 8 | Transient — dead time 1 | 2 | 3/5 | Dead 1 | 0.4 | I L3 | 0 | A | 0 | 50 |  | RECLOSE AT 0.400 s | Close at the end of the dead time | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 15 | V L1 | 57.735 | V | 0 | 50 |  | NO TRIP | A second fault inside this window goes to the next cycle | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 15 | V L2 | 57.735 | V | -120 | 50 |  | NO TRIP | A second fault inside this window goes to the next cycle | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 15 | V L3 | 57.735 | V | 120 | 50 |  | NO TRIP | A second fault inside this window goes to the next cycle | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 15 | I L1 | 0.45 | A | -25.84 | 50 |  | NO TRIP | A second fault inside this window goes to the next cycle | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 15 | I L2 | 0.45 | A | -145.84 | 50 |  | NO TRIP | A second fault inside this window goes to the next cycle | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 9 | Transient — reclaim | 2 | 4/5 | Reclaim | 15 | I L3 | 0.45 | A | 94.16 | 50 |  | NO TRIP | A second fault inside this window goes to the next cycle | no
79 | Auto-reclose | Automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | V L1 | 57.735 | V | 0 | 50 |  | RESET | A fault now counts as cycle 1 again | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | V L2 | 57.735 | V | -120 | 50 |  | RESET | A fault now counts as cycle 1 again | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | V L3 | 57.735 | V | 120 | 50 |  | RESET | A fault now counts as cycle 1 again | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | I L1 | 0.45 | A | -25.84 | 50 |  | RESET | A fault now counts as cycle 1 again | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | I L2 | 0.45 | A | -145.84 | 50 |  | RESET | A fault now counts as cycle 1 again | nu
79 | Auto-reclose | Automation | State Sequencer | sequence | 10 | Transient — reset confirmed | 2 | 5/5 | Reset | 3 | I L3 | 0.45 | A | 94.16 | 50 |  | RESET | A fault now counts as cycle 1 again | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I L1 | 0.105 | A | -72 | 50 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 1 | Detector — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | DETECTOR PICKED UP | Flag only, no trip without initiate | op
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO PICKUP | Detector must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO PICKUP | Detector must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO PICKUP | Detector must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I L1 | 0.095 | A | -72 | 50 |  | NO PICKUP | Detector must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | NO PICKUP | Detector must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 2 | Detector — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | NO PICKUP | Detector must drop out | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L1 | 0.3 | A | -72 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.150 s | Stage 1 | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 0.250 s | Stage 2 — trips the busbar zone | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 0.250 s | Stage 2 — trips the busbar zone | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 0.250 s | Stage 2 — trips the busbar zone | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I L1 | 0.3 | A | -72 | 50 |  | 0.250 s | Stage 2 — trips the busbar zone | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 0.250 s | Stage 2 — trips the busbar zone | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 4 | Busbar trip timing |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 0.250 s | Stage 2 — trips the busbar zone | nu
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L1 | 0 | A | -72 | 50 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Circuit-breaker failure | Automation | State Sequencer | sequence (assemble from these steps) | 5 | Reset check |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | NO TRIP | Proves the detector reset stops the scheme | no
74TC | Trip circuit supervision | Automation | — | binary / DC | 1 | Healthy circuit |  |  |  |  | (no injection) |  |  |  |  | Trip circuit intact, breaker closed | NO ALARM | Both binary inputs energised | no
74TC | Trip circuit supervision | Automation | — | binary / DC | 2 | Trip coil open |  |  |  |  | (no injection) |  |  |  |  | Open the trip-coil circuit at the terminal block | ALARM | After 2.000 s | op
74TC | Trip circuit supervision | Automation | — | binary / DC | 3 | Trip supply lost |  |  |  |  | (no injection) |  |  |  |  | Remove the DC supply to the trip circuit | ALARM | After 2.000 s | op
74TC | Trip circuit supervision | Automation | — | binary / DC | 4 | Breaker open |  |  |  |  | (no injection) |  |  |  |  | Breaker open with the circuit intact | NO ALARM | The scheme must not alarm on a normally open breaker — this is the point that catches a one-input arrangement wired as if it were two | no
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | V 4 | 57.735 | V | 0 | 50 | line side | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 1 | In synchronism |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | Δθ 12.0° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | Δθ 12.0° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | Δθ 12.0° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | V 4 | 57.735 | V | 12 | 50 | line side | CLOSE RELEASED | Δθ 12.0° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Δθ 12.0° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Δθ 12.0° | op
25 | Synchrocheck | Automation | Synchronizer | points | 2 | Angle inside limit |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Δθ 12.0° | op
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | Δθ 18.0° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Δθ 18.0° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Δθ 18.0° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | V 4 | 57.735 | V | 18 | 50 | line side | BLOCKED | Δθ 18.0° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | BLOCKED | Δθ 18.0° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | BLOCKED | Δθ 18.0° | no
25 | Synchrocheck | Automation | Synchronizer | points | 3 | Angle outside limit |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | BLOCKED | Δθ 18.0° | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | V 4 | 50.535 | V | 0 | 50 | line side | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 4 | Voltage difference outside |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | BLOCKED | ΔV 7.20 V | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | BLOCKED | Δf 0.096 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Δf 0.096 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Δf 0.096 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | V 4 | 57.735 | V | 0 | 50.096 | line side — 50.096 Hz | BLOCKED | Δf 0.096 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | BLOCKED | Δf 0.096 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | BLOCKED | Δf 0.096 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 5 | Slip outside limit |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | BLOCKED | Δf 0.096 Hz | no
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | V 4 | 10 | V | 0 | 50 | line side | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check | op
25 | Synchrocheck | Automation | Synchronizer | points | 6 | Dead line, live bus |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | CLOSE RELEASED | Release comes from the dead-line logic, not the sync check | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L1 | 43.879 | V | 0 | 50 | depressed phase | OPERATE | Operate after 3.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate after 3.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate after 3.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L1 | 48.497 | V | 0 | 50 | depressed phase | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× threshold |  |  |  |  | V L1 | 23.094 | V | 0 | 50 | depressed phase | 3.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 3.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 3.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 3.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 3.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 3.000 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L1 | 4 | V | 0 | 50 | depressed phase | BLOCKED | Function inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | BLOCKED | Function inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | BLOCKED | Function inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | BLOCKED | Function inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | BLOCKED | Function inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | BLOCKED | Function inhibited | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L1 | 66.684 | V | 0 | 50 | raised phase | OPERATE | Operate after 1.500 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Operate after 1.500 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Operate after 1.500 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Operate after 1.500 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate after 1.500 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate after 1.500 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L1 | 60.333 | V | 0 | 50 | raised phase | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× threshold |  |  |  |  | V L1 | 79.386 | V | 0 | 50 | raised phase | 1.500 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 1.500 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 1.500 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | 1.500 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | 1.500 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | 1.500 s | Definite time | nu
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L1 | 6.351 | V | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L2 | 6.351 | V | 120 | 50 |  | OPERATE | Operate after 3.000 s | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 1 | Threshold — above |  |  |  |  | V L3 | 6.351 | V | -120 | 50 |  | OPERATE | Operate after 3.000 s | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 1 | Threshold — above |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | Operate after 3.000 s | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L1 | 5.196 | V | 0 | 50 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L2 | 5.196 | V | 120 | 50 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 2 | Threshold — below |  |  |  |  | V L3 | 5.196 | V | -120 | 50 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 2 | Threshold — below |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | V2 = 57.74 V | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L2 | 57.735 | V | 120 | 50 |  | OPERATE | V2 = 57.74 V | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | V L3 | 57.735 | V | -120 | 50 |  | OPERATE | V2 = 57.74 V | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L1 | 0 | A | 0 | 50 |  | OPERATE | V2 = 57.74 V | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L2 | 0 | A | 0 | 50 |  | OPERATE | V2 = 57.74 V | op
47 | Voltage unbalance / phase rotation | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal |  |  |  |  | I L3 | 0 | A | 0 | 50 |  | OPERATE | V2 = 57.74 V | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L1 | 57.735 | V | 0 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L2 | 57.735 | V | -120 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | V L3 | 57.735 | V | 120 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I L1 | 0 | A | 0 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I L2 | 0 | A | 0 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Threshold — past |  |  |  |  | I L3 | 0 | A | 0 | 48.95 |  | OPERATE | Operate after 0.500 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L1 | 57.735 | V | 0 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L2 | 57.735 | V | -120 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | V L3 | 57.735 | V | 120 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I L1 | 0 | A | 0 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I L2 | 0 | A | 0 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Threshold — short of |  |  |  |  | I L3 | 0 | A | 0 | 49.05 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L1 | 57.735 | V | 0 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L2 | 57.735 | V | -120 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | V L3 | 57.735 | V | 120 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L1 | 0 | A | 0 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L2 | 0 | A | 0 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing |  |  |  |  | I L3 | 0 | A | 0 | 48.95 |  | 0.500 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L1 | 24 | V | 0 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L2 | 24 | V | -120 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | V L3 | 24 | V | 120 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L1 | 0 | A | 0 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L2 | 0 | A | 0 | 48.95 |  | BLOCKED | Function inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage |  |  |  |  | I L3 | 0 | A | 0 | 48.95 |  | BLOCKED | Function inhibited | no
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 1 | Rate above threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 | ramp to 47.00 Hz over 2.500 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 1 | Rate above threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 | ramp to 47.00 Hz over 2.500 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 1 | Rate above threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 | ramp to 47.00 Hz over 2.500 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 1 | Rate above threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 2.500 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 1 | Rate above threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 2.500 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 1 | Rate above threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 2.500 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 2 | Rate below threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 | ramp to 47.00 Hz over 3.750 s | RESTRAIN | No operation | no
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 2 | Rate below threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 | ramp to 47.00 Hz over 3.750 s | RESTRAIN | No operation | no
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 2 | Rate below threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 | ramp to 47.00 Hz over 3.750 s | RESTRAIN | No operation | no
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 2 | Rate below threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 3.750 s | RESTRAIN | No operation | no
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 2 | Rate below threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 3.750 s | RESTRAIN | No operation | no
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 2 | Rate below threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 3.750 s | RESTRAIN | No operation | no
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 3 | Well above threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 | ramp to 47.00 Hz over 1.000 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 3 | Well above threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 | ramp to 47.00 Hz over 1.000 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 3 | Well above threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 | ramp to 47.00 Hz over 1.000 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 3 | Well above threshold |  |  |  |  | I L1 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 1.000 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 3 | Well above threshold |  |  |  |  | I L2 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 1.000 s | OPERATE | Operate after 0.200 s of sustained rate | op
81R | Rate of frequency change | Voltage & frequency | Ramping | ramp | 3 | Well above threshold |  |  |  |  | I L3 | 0 | A | 0 | 50 | ramp to 47.00 Hz over 1.000 s | OPERATE | Operate after 0.200 s of sustained rate | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | I L1 | 0.0397 | A | 0 | 50 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | I L2 | 0.0397 | A | -120 | 50 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 1 | Above threshold |  |  |  |  | I L3 | 0.0397 | A | 120 | 50 |  | OPERATE | Balanced 3φ · 550.0 kW primary | op
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | I L1 | 0.0325 | A | 0 | 50 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | I L2 | 0.0325 | A | -120 | 50 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 2 | Below threshold |  |  |  |  | I L3 | 0.0325 | A | 120 | 50 |  | RESTRAIN | Balanced 3φ · 450.0 kW primary | no
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× threshold |  |  |  |  | V L1 | 57.735 | V | 0 | 50 |  | 2.000 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× threshold |  |  |  |  | V L2 | 57.735 | V | -120 | 50 |  | 2.000 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× threshold |  |  |  |  | V L3 | 57.735 | V | 120 | 50 |  | 2.000 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× threshold |  |  |  |  | I L1 | 0.0722 | A | 0 | 50 |  | 2.000 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× threshold |  |  |  |  | I L2 | 0.0722 | A | -120 | 50 |  | 2.000 s | Balanced 3φ · 1000.0 kW primary | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× threshold |  |  |  |  | I L3 | 0.0722 | A | 120 | 50 |  | 2.000 s | Balanced 3φ · 1000.0 kW primary | nu

## Build guide
Building the 7SJ85 test plan in Test Universe
Assembles `7SJ85-SIP-steps.csv` and `7SJ85-SIP-channels.csv` into one Test Universe
document — 26 functions, 125 steps. Build it once and save it as a template.
Values below are for the tool's **sample** feeder: 20 kV, 50 Hz, **resonant earthed**
(Petersen coil), 180 A load at 0.9 pf, 12 km overhead at 0.12 Ω/km ∠72° positive and
0.38 Ω/km ∠68° zero sequence, phase CT 400:1, core-balance CT 60:1, VT 20000:100 wye with
3V0 from a broken-delta winding. Enter your real feeder in `7SJ85.html` and re-run the
generator.
---
1 · It is a SIPROTEC, not a Multilin
Three differences change how you build the document, and none of them are cosmetic.
**Function groups, not element numbers.** The device organises settings under function
groups; the ANSI numbers in this plan are the tool's labels for them. Each step's `FG`
reference in the tool names the group the setting actually lives in — carry that into the
test document's step names so a technician can find the setting in DIGSI without guessing.
**Ground-fault compensation is RE/RL and XE/XL, not k0.** The device wants two real
numbers, not one complex one. The sample line gives:
¦ Quantity ¦ Value ¦
¦---¦---¦
¦ RE/RL ¦ 0.9463 ¦
¦ XE/XL ¦ 0.6957 ¦
¦ k0, for cross-checking ¦ 0.7234 ∠−5.84° ¦
The tool computes all three from the same line constants so you can check the pair in
DIGSI against the k0 you would have set on a North American relay. If they disagree, the
line constants are wrong, not the conversion.
**The earthing decides which ground-fault function is real.** On a resonant-earthed network
the Petersen coil cancels the capacitive current and what is left on the faulted feeder is
a small **watt-metric** component. That is 67Ns, it works in milliamps, and it is the
function this device is usually bought for. Sections 5 and 6 are about it.
2 · Test object
¦ Field ¦ Sample value ¦ Where it comes from ¦
¦-------¦--------------¦---------------------¦
¦ Nominal voltage, secondary ¦ 100 V L–L (57.735 V L–N) ¦ VT 20000 : 100 ¦
¦ Nominal current, secondary ¦ 1 A ¦ CT 400 : 1 ¦
¦ VT ratio ¦ 200 : 1 ¦ ¦
¦ CT ratio, phase ¦ 400 : 1 ¦ ¦
¦ CT ratio, core balance ¦ 60 : 1 ¦ separate input ¦
¦ Nominal frequency ¦ 50 Hz ¦ ¦
¦ Line angle ¦ 72° ¦ Z1 angle ¦
¦ Z1 secondary, whole line ¦ 2.880 Ω ¦ `z1m · len · CTR/VTR` ¦
¦ Z0 secondary, whole line ¦ 9.120 Ω ¦ same conversion ¦
¦ RE/RL, XE/XL ¦ 0.9463 / 0.6957 ¦ from Z0 and Z1 ¦
Note the **1 A** secondary. Every current in this plan is small by North American habit,
and the ground-fault work is smaller still. Confirm the relay is a 1 A unit before you
wire anything.
3 · Hardware configuration
**Amplifier mode: 3 × 32 A**, and it is not close — the largest current anywhere in the
plan is 16.000 A, on the 50-2 timing shot. Nothing here needs a second triple and nothing
comes near a channel limit. That is worth knowing up front, because it means you can build
the whole document in one hardware configuration.
Four analogue connections, and two of them are shared:
¦ Channel ¦ Carries ¦ Used by ¦
¦---¦---¦---¦
¦ V L1–L3 ¦ Phase voltages ¦ most functions ¦
¦ I L1–L3 ¦ Phase currents ¦ most functions ¦
¦ **I aux** ¦ Core-balance residual, 3I0 ¦ 67Ns, 50N-*, 51N ¦
¦ **V 4** ¦ Broken-delta 3V0 **or** synchrocheck line side ¦ 67Ns, 59N — and 25 ¦
**V 4 cannot serve both jobs at once.** The 67Ns and 59N steps drive it as the
broken-delta displacement voltage at 180°; the 25 steps drive it as the line-side voltage
near 0° with its own frequency. That is a re-patch at the terminal block, not a software
change, so build the plan in two blocks with the change between them and say so in the
document. Section 4 orders the modules accordingly.
`I aux` is a separate physical input from the phase currents. Injecting the residual into
a phase CT proves nothing about a core-balance function, and a reversed core-balance CT
turns every forward 67Ns point into a reverse one — which looks exactly like a threshold
problem and is not one.
Binary I/O
¦ CMC ¦ Direction ¦ To / from the relay ¦
¦-----¦-----------¦---------------------¦
¦ Bin. in 1 ¦ in ¦ Trip — timing reference for every operate time ¦
¦ Bin. in 2 ¦ in ¦ Close output — 79 and the 25 permissive ¦
¦ Bin. in 3 ¦ in ¦ Pickup / start indication ¦
¦ Bin. out 1 ¦ out ¦ 52a breaker simulation ¦
¦ Bin. out 2 ¦ out ¦ 52b breaker simulation ¦
¦ Bin. out 3 ¦ out ¦ Breaker-failure initiate ¦
The 52a/52b pair is required for the 79 sequence: the scheme tracks breaker position to
know whether its close took, and without it the reclose declares a close failure part-way
through and the later shots never run.
4 · Module map
Filter `7SJ85-SIP-steps.csv` on `TU_Module`. Ordered so V 4 is patched once, in the middle:
¦ Order ¦ Module ¦ Elements ¦ Steps ¦
¦------:¦--------¦----------¦------:¦
¦ 1 ¦ Overcurrent — pickup + time ¦ 50-1, 50-2, 50N-1, 50N-2, 37 ¦ 16 ¦
¦ 2 ¦ Overcurrent — characteristic ¦ 51, 51N, 46, 49 ¦ 19 ¦
¦ 3 ¦ Voltage ¦ 27, 59 ¦ 7 ¦
¦ 4 ¦ Harmonics ¦ Inrush ¦ 4 ¦
¦ 5 ¦ Advanced Distance ¦ 21, FLOC ¦ 11 ¦
¦ 6 ¦ Ramping ¦ 67 (6 points), 81R (3 ramps) ¦ 9 ¦
¦ 7 ¦ State Sequencer ¦ 79 (10 sequenced) · 50BF (5 assembled) ¦ 15 ¦
¦ — ¦ *re-patch V 4 to broken delta* ¦ ¦ ¦
¦ 8 ¦ Quick CMC ¦ 67Ns, 59N, 51V, 47, 81, 32 ¦ 34 ¦
¦ — ¦ *re-patch V 4 to line side* ¦ ¦ ¦
¦ 9 ¦ Synchronizer ¦ 25 ¦ 6 ¦
¦ 10 ¦ — (no injection) ¦ 74TC ¦ 4 ¦
74TC is not an analogue test. It is trip-circuit continuity at the terminal block,
evidenced by the device's own supervision alarm: prove it healthy with the breaker closed,
then open the trip-coil circuit and confirm the alarm. It sits in the plan so it is not
forgotten, not so it can be injected.
5 · 67Ns — the function that is not tested at 90°
This is the one worth building carefully, and the one most likely to be recorded wrong.
The sample settings: 3V0 threshold 20.0 V, applied 100.0 V; test residual 60.0 mA;
watt-metric component threshold 15.0 mA; cos φ measurement; 1 s delay.
**The operate sector does not run to ±90° from the characteristic axis.** It runs to where
the measured component falls to its threshold, which is `arccos(component / ¦3I0¦)` — with
these values, **±75.5°**. A point placed at 82° from the axis, which reads as comfortably
inside a 90° sector, will restrain, and it should. The plan's sector-edge points are placed
either side of 75.5°, not 90°, and the tool recomputes the edge when you change either
threshold.
**Everything here is in milliamps.** 60 mA applied against a 15 mA component threshold.
Confirm the amplifier's accuracy at that output before treating a marginal result as a
relay problem, and confirm the core-balance CT ratio and direction before treating a
failed forward point as a threshold.
**Run forward and reverse first.** If both fail, the core-balance CT is reversed or the CT
star point on the tool's Setup tab does not match the drawing. Chase that before spending
an hour on sector edges.
**cos φ or sin φ is a network question, not a preference.** cos φ (watt-metric) belongs on
a resonant-earthed network like this one, where the coil has cancelled the capacitive
current. sin φ (var-metric) belongs on an isolated network, where the capacitive current
is the signal. The tool checks the pairing against the earthing on the Setup tab and says
so; if the network on your job is isolated and the function is set to cos φ, that is a
finding, not a test point.
6 · 59N — measures correctly, selects nothing
Displacement voltage appears on **every feeder** on the galvanically connected network,
not only the faulted one. A 59N pass says the device measures 3V0 correctly. It says
nothing about which feeder is faulted, and it should not be recorded as ground-fault
protection. That is 67Ns's job.
The phase voltages in the 59N steps are a real displaced set — the neutral shifted toward
the faulted phase — rather than three independent numbers, so the relay sees a consistent
picture. Coverage in the sample is 20 % of full displacement at the 20.0 V threshold.
7 · Inrush restraint — the blocked case is the test
The 2nd harmonic goes on the **same physical channel** as the fundamental, superimposed:
100 Hz on top of 50 Hz. Build it in the Harmonics module, or as a superimposed signal in
State Sequencer.
A clean fundamental injection — which is what every ordinary overcurrent test applies —
contains no 2nd harmonic and always releases the stage. So an overcurrent test passing
proves nothing about inrush restraint. The four steps are: below the ratio threshold
(releases), above it (blocks), the ratio boundary at 15.0 % (450.0 mA of harmonic on
3.0000 A of fundamental), and the **upper-limit release at 8 × In**, where blocking is
withdrawn so a genuine fault during energisation is not held off indefinitely. That last
step is the one people skip and the one that matters at two in the morning.
8 · Distance and fault location
21 uses the **phase loop** — (V L2 − V L3)/(I L2 − I L3), no residual term — so RE/RL and
XE/XL play no part in it. FLOC uses the ground loop and they play every part. That
asymmetry is the diagnostic: **phase reaches correct and ground results drifting means the
ground-fault compensation or Z0 is wrong, not the device.**
Reaches are entered as a percentage of the line, so they depend on the line constants as
much as on the relay. Confirm Z1 (2.880 Ω secondary) and the 72° angle against the
line-constants sheet before accepting any zone result.
For FLOC there is no trip to time — read the device's own reported distance out of its
fault record. The acceptance window in the sample is ±0.60 km on a 12.00 km line.
9 · Before you inject
- Every quantity is **secondary at the device terminals**; angles in degrees,
counter-clockwise positive, V L1 at 0°.
- Confirm the device is a **1 A** unit.
- Confirm the **CT star-point direction** in DIGSI against the drawing before any
directional test — 67, 67Ns and 32 all depend on it and all fail the same way when it is
wrong.
- Check one 51 timing point against the device's own prediction before accepting the
rest. Curve constants move between firmware revisions, and if the first point disagrees
every other time in the table is wrong by the same factor.
- Negative-sequence rows (46) already carry the ×3 a single-phase injection needs. Do not
apply it again.
10 · After the first build
Save as a template with the test object detached. The module order, the V 4 re-patch point
and the binary map carry across feeders unchanged; the line constants, thresholds and the
67Ns sector edge come out of the generator.
Two things this plan deliberately will not do: it will not let a 59N pass stand as
ground-fault protection, and it will not place the 67Ns sector edge at 90° because that is
where the drawing suggests it should be.