## Start here
889-GEN — Multilin 889 generator protection
How to use this workbook
Fill in | Only the two shaded columns on each test sheet: MEASURED and PASS / FAIL. Everything else is calculated and should not be edited by hand.
Example row | MEASURED "1.432 s", PASS / FAIL "PASS". Use the same unit the Expected column uses, so the two can be compared without conversion.
Untested steps | Record them as NOT TESTED with a reason. A blank result reads as work not yet done; it must never be left blank on a completed record.
If a setting changes | Do not edit numbers here. Change it in the relay tool, re-run the generator, and rebuild this workbook — that is what keeps the injected values and the calculations from drifting apart.
Where these values come from
Plan | 889-GEN — Multilin 889 generator protection
Generated | generated 2026-09-15 00:33 from 889.html
Configuration | mva=100; kv=13.8; pf=0.85; freq=60; rot=ABC; poles=2; xd=1.8; xdp=0.25; xdpp=0.18; x2=0.2; cttp=5000; ctts=5; ctnp=5000; ctns=5; ctgp=200; ctgs=5; vtp=13800; vts=120; vtc=wye; zsrc=I; zhold=5; ngtp=7970; ngts=240; gnd=hr; cmc=6x; imax=12.5; vmax=300
Conventions | All quantities are SECONDARY at the relay terminals. Angles in degrees, CCW positive, V L1 = 0.
Sample data | Values shown are for the tool's sample configuration — re-generate after entering real station data.
Record identification
Station
Feeder / plant item
Device serial
Firmware
Setting file revision
Test set serial
Tested by
Date
Witnessed by
Sheets in this workbook
Test steps | 137 test steps — the record. Fill in MEASURED and PASS / FAIL.
Channels | 1147 rows — one per channel per step, for pasting into a Test Universe module table.
Build guide | How to assemble this plan in Test Universe, and the thing about this relay most likely to be got wrong.
Progress
Total steps
Results entered
Passed
Failed
Not tested
Outstanding
Counts refer to the first test sheet only.

## Test steps
Function | Description | TU module | Drive as | # | Test step | What is applied | V L1 | V L2 | V L3 | V 4 | I L1 | I L2 | I L3 | I B-L1 | I B-L2 | I B-L3 | Hz | Reachable | Expected | Expected — detail | MEASURED | PASS / FAIL
87G | Generator differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | Idiff required 0.100 pu · applied 0.110 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0918@0.0 | 2.0918@-120.0 | 2.0918@120.0 | 1.6316@180.0 | 1.6316@60.0 | 1.6316@-60.0 | 60 | yes | OPERATE | IT 0.500 pu · IN 0.390 pu
87G | Generator differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | Idiff required 0.100 pu · applied 0.090 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0918@0.0 | 2.0918@-120.0 | 2.0918@120.0 | 1.7153@180.0 | 1.7153@60.0 | 1.7153@-60.0 | 60 | yes | RESTRAIN | IT 0.500 pu · IN 0.410 pu
87G | Generator differential | Differential | characteristic | 3 | Irest 1 pu — above slope | Idiff required 0.100 pu · applied 0.110 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 4.1837@0.0 | 4.1837@-120.0 | 4.1837@120.0 | 3.7235@180.0 | 3.7235@60.0 | 3.7235@-60.0 | 60 | yes | OPERATE | IT 1.000 pu · IN 0.890 pu
87G | Generator differential | Differential | characteristic | 4 | Irest 1 pu — below slope | Idiff required 0.100 pu · applied 0.090 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 4.1837@0.0 | 4.1837@-120.0 | 4.1837@120.0 | 3.8072@180.0 | 3.8072@60.0 | 3.8072@-60.0 | 60 | yes | RESTRAIN | IT 1.000 pu · IN 0.910 pu
87G | Generator differential | Differential | characteristic | 5 | Irest 3 pu — above slope | Idiff required 0.300 pu · applied 0.330 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.5511@0.0 | 12.5511@-120.0 | 12.5511@120.0 | 11.1705@180.0 | 11.1705@60.0 | 11.1705@-60.0 | 60 | yes | OPERATE | IT 3.000 pu · IN 2.670 pu
87G | Generator differential | Differential | characteristic | 6 | Irest 3 pu — below slope | Idiff required 0.300 pu · applied 0.270 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.5511@0.0 | 12.5511@-120.0 | 12.5511@120.0 | 11.4215@180.0 | 11.4215@60.0 | 11.4215@-60.0 | 60 | yes | RESTRAIN | IT 3.000 pu · IN 2.730 pu
87G | Generator differential | Differential | characteristic | 7 | Irest 7 pu — above slope | Idiff required 1.100 pu · applied 1.210 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 29.2859@0.0 | 29.2859@-120.0 | 29.2859@120.0 | 24.2236@180.0 | 24.2236@60.0 | 24.2236@-60.0 | 60 | yes | OPERATE | IT 7.000 pu · IN 5.790 pu
87G | Generator differential | Differential | characteristic | 8 | Irest 7 pu — below slope | Idiff required 1.100 pu · applied 0.990 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 29.2859@0.0 | 29.2859@-120.0 | 29.2859@120.0 | 25.1440@180.0 | 25.1440@60.0 | 25.1440@-60.0 | 60 | yes | RESTRAIN | IT 7.000 pu · IN 6.010 pu
87GN | Restricted ground fault | Quick CMC | points | 1 | Sensitivity — above pickup | Ground CT input only, phase CTs at zero. Applied 0.110 ×CT. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.5500@0.0 | [5 empty] | 60 | yes | OPERATE | Operate time 0.00 s
87GN | Restricted ground fault | Quick CMC | points | 2 | Sensitivity — below pickup | Ground CT input only, phase CTs at zero. Applied 0.090 ×CT. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.4500@0.0 | [5 empty] | 60 | yes | RESTRAIN | Operate time 0.00 s
87GN | Restricted ground fault | Quick CMC | points | 3 | Through-fault stability | Phase L1 and the ground input driven in opposition at 4 ×CT — an external ground fault. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 20.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 500.0000@180.0 |  |  | 60 | yes | RESTRAIN | No operation anywhere on the ramp
59N | Stator ground — fundamental | Quick CMC | points | 1 | Pickup — above threshold | 5.50 V at the neutral input · equivalent to a fault 2.3% up the winding | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 5.500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Operate after 0.50 s
59N | Stator ground — fundamental | Quick CMC | points | 2 | Pickup — below threshold | 4.50 V at the neutral input · equivalent to a fault 1.9% up the winding | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 4.500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | RESTRAIN | No operation
59N | Stator ground — fundamental | Quick CMC | points | 3 | Fault 100% from neutral | Drives 239.92 V at the relay | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 239.923@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Detected by 59N
59N | Stator ground — fundamental | Quick CMC | points | 4 | Fault 50% from neutral | Drives 119.96 V at the relay | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 119.961@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Detected by 59N
59N | Stator ground — fundamental | Quick CMC | points | 5 | Fault 10% from neutral | Drives 23.99 V at the relay | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 23.992@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Detected by 59N
59N | Stator ground — fundamental | Quick CMC | points | 6 | Fault 5% from neutral | Drives 12.00 V at the relay | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 11.996@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Detected by 59N
27TN | Stator ground — third harmonic | Harmonics | points | 1 | Above threshold — healthy | Third harmonic held 10% above the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.550@0.0 | 0.4184@0.0 | 0.4184@-120.0 | 0.4184@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | Element must not operate
27TN | Stator ground — third harmonic | Harmonics | points | 2 | Below threshold — fault | Third harmonic dropped 10% below the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.450@0.0 | 0.4184@0.0 | 0.4184@-120.0 | 0.4184@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 1.0 s
27TN | Stator ground — third harmonic | Harmonics | points | 3 | Third harmonic removed | Neutral input taken to zero — the deepest condition | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.000@0.0 | 0.4184@0.0 | 0.4184@-120.0 | 0.4184@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 1.0 s
27TN | Stator ground — third harmonic | Harmonics | points | 4 | Supervision withdrawn | Third harmonic at zero but the machine off load — proves the element stays blocked when it has no basis to measure | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 0.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | Element inhibited
40 | Loss of excitation | Advanced Distance | shots | 1 | Circle centre | Deepest point inside zone 1 — 10.35 Ω on the −X axis | 51.750@0.0 | 51.750@-120.0 | 51.750@120.0 |  | 5.0000@90.0 | 5.0000@-30.0 | 5.0000@-150.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.10 s
40 | Loss of excitation | Advanced Distance | shots | 2 | Boundary top — inside | 8% inside the circle · Z = 2.73 Ω −90.0° | 13.662@0.0 | 13.662@-120.0 | 13.662@120.0 |  | 5.0000@90.0 | 5.0000@-30.0 | 5.0000@-150.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.10 s
40 | Loss of excitation | Advanced Distance | shots | 3 | Boundary top — outside | 8% outside the circle · Z = 1.41 Ω −90.0° | 7.038@0.0 | 7.038@-120.0 | 7.038@120.0 |  | 5.0000@90.0 | 5.0000@-30.0 | 5.0000@-150.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
40 | Loss of excitation | Advanced Distance | shots | 4 | Boundary bottom — inside | 8% inside the circle · Z = 17.97 Ω −90.0° | 89.838@0.0 | 89.838@-120.0 | 89.838@120.0 |  | 5.0000@90.0 | 5.0000@-30.0 | 5.0000@-150.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.10 s
40 | Loss of excitation | Advanced Distance | shots | 5 | Boundary bottom — outside | 8% outside the circle · Z = 19.29 Ω −90.0° | 96.462@0.0 | 96.462@-120.0 | 96.462@120.0 |  | 5.0000@90.0 | 5.0000@-30.0 | 5.0000@-150.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
40 | Loss of excitation | Advanced Distance | shots | 6 | Boundary right — inside | 8% inside the circle · Z = 12.85 Ω −53.6° | 64.255@0.0 | 64.255@-120.0 | 64.255@120.0 |  | 5.0000@53.6 | 5.0000@-66.4 | 5.0000@173.6 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.10 s
40 | Loss of excitation | Advanced Distance | shots | 7 | Boundary right — outside | 8% outside the circle · Z = 13.68 Ω −49.2° | 68.390@0.0 | 68.390@-120.0 | 68.390@120.0 |  | 5.0000@49.2 | 5.0000@-70.8 | 5.0000@169.2 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
40 | Loss of excitation | Advanced Distance | shots | 8 | Boundary left — inside | 8% inside the circle · Z = 12.85 Ω −126.4° | 64.255@0.0 | 64.255@-120.0 | 64.255@120.0 |  | 5.0000@126.4 | 5.0000@6.4 | 5.0000@-113.6 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.10 s
40 | Loss of excitation | Advanced Distance | shots | 9 | Boundary left — outside | 8% outside the circle · Z = 13.68 Ω −130.8° | 68.390@0.0 | 68.390@-120.0 | 68.390@120.0 |  | 5.0000@130.8 | 5.0000@10.8 | 5.0000@-109.2 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
40 | Loss of excitation | Advanced Distance | shots | 10 | Normal excitation | Positive reactance, machine exporting VARs — well clear of the characteristic | 82.800@0.0 | 82.800@-120.0 | 82.800@120.0 |  | 5.0000@-90.0 | 5.0000@150.0 | 5.0000@30.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
46 | Negative-sequence capability | Overcurrent | characteristic | 1 | Pickup — above threshold | I2 = 0.088 pu · single phase, so 1.104 A applied | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.1045@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Very long operate time at this level
46 | Negative-sequence capability | Overcurrent | characteristic | 2 | Pickup — below threshold | I2 = 0.072 pu · single phase, so 0.904 A applied | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.9037@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
46 | Negative-sequence capability | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | K / I2² = 444.4 s | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.8827@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 444.4 s | 7.41 minutes
46 | Negative-sequence capability | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | K / I2² = 250.0 s | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.5102@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 250.0 s | 4.17 minutes
46 | Negative-sequence capability | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | K / I2² = 111.1 s | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.7653@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 111.1 s | 1.85 minutes
46 | Negative-sequence capability | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | K / I2² = 40.0 s | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.2755@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 40.0 s | 0.67 minutes
32 | Reverse / low forward power | Quick CMC | points | 1 | Above threshold — motoring | 120% of setting, power into the machine | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0427@180.0 | 0.0427@60.0 | 0.0427@-60.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary
32 | Reverse / low forward power | Quick CMC | points | 2 | Below threshold | 80% of setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0284@180.0 | 0.0284@60.0 | 0.0284@-60.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary
32 | Reverse / low forward power | Quick CMC | points | 3 | Timing at 2× pickup | Long definite time — this element is deliberately slow | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0711@180.0 | 0.0711@60.0 | 0.0711@-60.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary
21 | Distance backup | Advanced Distance | shots | 1 | Reach at MTA — inside | Boundary here is 19.87 Ω · applied 18.28 Ω +85.0° | 69.282@90.0 | 91.411@0.0 | 91.411@180.0 |  | 0.0000@0.0 | 5.0000@-85.0 | 5.0000@95.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.50 s
21 | Distance backup | Advanced Distance | shots | 2 | Reach at MTA — outside | Boundary here is 19.87 Ω · applied 21.46 Ω +85.0° | 69.282@90.0 | 107.309@0.0 | 107.309@180.0 |  | 0.0000@0.0 | 5.0000@-85.0 | 5.0000@95.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
21 | Distance backup | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | Boundary here is 17.21 Ω · applied 15.83 Ω +115.0° | 69.282@90.0 | 79.164@0.0 | 79.164@180.0 |  | 0.0000@0.0 | 5.0000@-115.0 | 5.0000@65.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.50 s
21 | Distance backup | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | Boundary here is 17.21 Ω · applied 18.59 Ω +115.0° | 69.282@90.0 | 92.932@0.0 | 92.932@180.0 |  | 0.0000@0.0 | 5.0000@-115.0 | 5.0000@65.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
21 | Distance backup | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | Boundary here is 17.21 Ω · applied 15.83 Ω +55.0° | 69.282@90.0 | 79.164@0.0 | 79.164@180.0 |  | 0.0000@0.0 | 5.0000@-55.0 | 5.0000@125.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 0.50 s
21 | Distance backup | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | Boundary here is 17.21 Ω · applied 18.59 Ω +55.0° | 69.282@90.0 | 92.932@0.0 | 92.932@180.0 |  | 0.0000@0.0 | 5.0000@-55.0 | 5.0000@125.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
78 | Out of step | Advanced Distance | shots | 1 | Right of the right blinder | R = 12.42 Ω — outside, where a swing starts | 62.100@0.0 | 62.100@-120.0 | 62.100@120.0 |  | 5.0000@0.0 | 5.0000@-120.0 | 5.0000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OUTSIDE | Outside the blinder pair
78 | Out of step | Advanced Distance | shots | 2 | Inside the right blinder | R = 7.45 Ω — first blinder crossed | 37.260@0.0 | 37.260@-120.0 | 37.260@120.0 |  | 5.0000@0.0 | 5.0000@-120.0 | 5.0000@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | INSIDE | Inside the blinder pair
78 | Out of step | Advanced Distance | shots | 3 | Inside the left blinder | R = −7.45 Ω — still between the blinders | 37.260@0.0 | 37.260@-120.0 | 37.260@120.0 |  | 5.0000@180.0 | 5.0000@60.0 | 5.0000@-60.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | INSIDE | Inside the blinder pair
78 | Out of step | Advanced Distance | shots | 4 | Left of the left blinder | R = −12.42 Ω — second blinder crossed, pole slip complete | 62.100@0.0 | 62.100@-120.0 | 62.100@120.0 |  | 5.0000@180.0 | 5.0000@60.0 | 5.0000@-60.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OUTSIDE | Outside the blinder pair
50/27 | Inadvertent energization | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | Voltage at nominal, no current. Hold well past the arming delay. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | DISARMED | Arming flag must stay dropped
50/27 | Inadvertent energization | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | Full current applied with voltage still at nominal | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 5.0000@165.0 | 5.0000@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | NO TRIP | This is the step that catches a scheme armed by mistake
50/27 | Inadvertent energization | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | Voltage below the arming threshold, held for 5.0 s | 27.713@0.0 | 27.713@-120.0 | 27.713@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | ARMS | Arming flag picks up after 5.0 s
50/27 | Inadvertent energization | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | Armed, but current short of the detector | 27.713@0.0 | 27.713@-120.0 | 27.713@120.0 |  | 2.2500@-75.0 | 2.2500@165.0 | 2.2500@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | NO TRIP | 90% of pickup
50/27 | Inadvertent energization | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | Armed, current past the detector — the real event | 27.713@0.0 | 27.713@-120.0 | 27.713@120.0 |  | 2.7500@-75.0 | 2.7500@165.0 | 2.7500@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | TRIP | Instantaneous, no intentional delay
50/27 | Inadvertent energization | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | Restore voltage, wait past 0.25 s, then re-apply current | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 5.0000@165.0 | 5.0000@45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | NO TRIP | Proves the scheme disarms on restoration
51V | Voltage-restrained OC | Quick CMC | points | 1 | V = 1 ×VT — above pickup | Effective pickup 7.500 A sec at 69.28 V | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.8750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Curve runs from here
51V | Voltage-restrained OC | Quick CMC | points | 2 | V = 1 ×VT — below pickup | Effective pickup 7.500 A sec at 69.28 V | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.1250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51V | Voltage-restrained OC | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Multiple is of the effective pickup, not the nominal one
51V | Voltage-restrained OC | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | Effective pickup 5.625 A sec at 51.96 V | 51.962@0.0 | 51.962@-120.0 | 51.962@120.0 |  | 5.9063@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Curve runs from here
51V | Voltage-restrained OC | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | Effective pickup 5.625 A sec at 51.96 V | 51.962@0.0 | 51.962@-120.0 | 51.962@120.0 |  | 5.3438@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51V | Voltage-restrained OC | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | IEEE Very Inv · TDM 0.20 | 51.962@0.0 | 51.962@-120.0 | 51.962@120.0 |  | 11.2500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Multiple is of the effective pickup, not the nominal one
51V | Voltage-restrained OC | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | Effective pickup 3.750 A sec at 34.64 V | 34.641@0.0 | 34.641@-120.0 | 34.641@120.0 |  | 3.9375@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Curve runs from here
51V | Voltage-restrained OC | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | Effective pickup 3.750 A sec at 34.64 V | 34.641@0.0 | 34.641@-120.0 | 34.641@120.0 |  | 3.5625@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51V | Voltage-restrained OC | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | IEEE Very Inv · TDM 0.20 | 34.641@0.0 | 34.641@-120.0 | 34.641@120.0 |  | 7.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Multiple is of the effective pickup, not the nominal one
51V | Voltage-restrained OC | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | Effective pickup 1.875 A sec at 17.32 V | 17.321@0.0 | 17.321@-120.0 | 17.321@120.0 |  | 1.9688@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Curve runs from here
51V | Voltage-restrained OC | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | Effective pickup 1.875 A sec at 17.32 V | 17.321@0.0 | 17.321@-120.0 | 17.321@120.0 |  | 1.7813@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51V | Voltage-restrained OC | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | IEEE Very Inv · TDM 0.20 | 17.321@0.0 | 17.321@-120.0 | 17.321@120.0 |  | 3.7500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Multiple is of the effective pickup, not the nominal one
24 | Volts per hertz | Quick CMC | points | 1 | 60 Hz — above threshold | 1.155 pu V/Hz needs 80.02 V secondary at 60 Hz | 80.021@0.0 | 80.021@-120.0 | 80.021@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Operate after 20.00 s
24 | Volts per hertz | Quick CMC | points | 2 | 60 Hz — below threshold | 1.045 pu V/Hz needs 72.40 V secondary at 60 Hz | 72.400@0.0 | 72.400@-120.0 | 72.400@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | RESTRAIN | No operation
24 | Volts per hertz | Quick CMC | points | 3 | 57 Hz — above threshold | 1.155 pu V/Hz needs 76.02 V secondary at 57 Hz | 76.020@0.0 | 76.020@-120.0 | 76.020@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 57 | yes | OPERATE | Operate after 20.00 s
24 | Volts per hertz | Quick CMC | points | 4 | 57 Hz — below threshold | 1.045 pu V/Hz needs 68.78 V secondary at 57 Hz | 68.780@0.0 | 68.780@-120.0 | 68.780@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 57 | yes | RESTRAIN | No operation
24 | Volts per hertz | Quick CMC | points | 5 | 54 Hz — above threshold | 1.155 pu V/Hz needs 72.02 V secondary at 54 Hz | 72.019@0.0 | 72.019@-120.0 | 72.019@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 54 | yes | OPERATE | Operate after 20.00 s
24 | Volts per hertz | Quick CMC | points | 6 | 54 Hz — below threshold | 1.045 pu V/Hz needs 65.16 V secondary at 54 Hz | 65.160@0.0 | 65.160@-120.0 | 65.160@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 54 | yes | RESTRAIN | No operation
24 | Volts per hertz | Quick CMC | points | 7 | Timing at 1.2× pickup | 1.320 pu V/Hz at nominal frequency | 91.452@0.0 | 91.452@-120.0 | 91.452@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | 5.00 s | From the inverse characteristic
24 | Volts per hertz | Quick CMC | points | 8 | Timing at 1.5× pickup | 1.650 pu V/Hz at nominal frequency | 114.315@0.0 | 114.315@-120.0 | 114.315@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | 2.00 s | From the inverse characteristic
55 | Power factor | Quick CMC | points | 1 | Past the limit | 5° beyond the setting angle | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0918@23.2 | 2.0918@-96.8 | 2.0918@143.2 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | pf = 0.919 leading
55 | Power factor | Quick CMC | points | 2 | Short of the limit | 5° inside the setting angle | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0918@13.2 | 2.0918@-106.8 | 2.0918@133.2 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | pf = 0.974 leading
55 | Power factor | Quick CMC | points | 3 | Full VAR, no watts | Current in quadrature — power factor zero | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0918@90.0 | 2.0918@-30.0 | 2.0918@-150.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | pf = 0.000 leading
55 | Power factor | Quick CMC | points | 4 | Below minimum current | Same angle, current dropped under the 0.20 × supervision | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.6694@23.2 | 0.6694@-96.8 | 0.6694@143.2 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | pf = 0.919 leading
49 | Stator thermal overload | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | Applied 5.271 A sec · prior load 0.80× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.2715@-25.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 602.6 s | 10.04 minutes
49 | Stator thermal overload | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | Applied 6.589 A sec · prior load 0.80× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.5893@-25.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 260.4 s | 4.34 minutes
49 | Stator thermal overload | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | Applied 8.786 A sec · prior load 0.80× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 8.7858@-25.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 117.8 s | 1.96 minutes
49 | Stator thermal overload | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | Applied 13.179 A sec · prior load 0.80× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 13.1786@-25.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 46.0 s | 0.77 minutes
50P | Phase instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 21.000 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 21.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50P | Phase instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 19.000 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 19.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50P | Phase instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2× pickup | Step from prefault zero straight to the test value | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 40.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.050 s | Measured from application of current to trip
51P | Phase time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 5.775 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.7750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51P | Phase time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 5.225 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.2250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51P | Phase time OC | Overcurrent | characteristic | 3 | Timing at 2× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 11.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Predicted from the curve equation
51P | Phase time OC | Overcurrent | characteristic | 4 | Timing at 3× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 16.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.588 s | Predicted from the curve equation
51P | Phase time OC | Overcurrent | characteristic | 5 | Timing at 5× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 27.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.262 s | Predicted from the curve equation
50G | Ground instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 2.625 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50G | Ground instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 2.375 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.3750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50G | Ground instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2× pickup | Step from prefault zero straight to the test value | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.050 s | Measured from application of current to trip
51G | Ground time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.050 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.0500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51G | Ground time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 0.950 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.9500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51G | Ground time OC | Overcurrent | characteristic | 3 | Timing at 2× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 4 | Timing at 3× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.588 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 5 | Timing at 5× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.262 s | Predicted from the curve equation
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 2.625 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 2.375 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.3750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2× pickup | Step from prefault zero straight to the test value | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.050 s | Measured from application of current to trip
51N | Neutral time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.050 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.0500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — let the curve run out
51N | Neutral time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 0.950 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.9500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51N | Neutral time OC | Overcurrent | characteristic | 3 | Timing at 2× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.406 s | Predicted from the curve equation
51N | Neutral time OC | Overcurrent | characteristic | 4 | Timing at 3× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.588 s | Predicted from the curve equation
51N | Neutral time OC | Overcurrent | characteristic | 5 | Timing at 5× pickup | IEEE Very Inv · TDM 0.20 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.262 s | Predicted from the curve equation
67 | Directional supervision | Ramping | points | 1 | Forward maximum torque | Current at the characteristic angle — deepest into the operate zone. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 11.0000@-45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 2 | Reverse maximum torque | Rotated 180° from MTA. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 11.0000@135.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 3 | Boundary, leading side (inside) | 5° inside the boundary. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 11.0000@40.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 4 | Boundary, leading side (outside) | 5° outside. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 11.0000@50.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 5 | Boundary, lagging side (inside) | 5° inside the boundary. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 11.0000@-130.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup
67 | Directional supervision | Ramping | points | 6 | Boundary, lagging side (outside) | 5° outside. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 11.0000@-140.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup
27 | Undervoltage | Voltage | pickup+time | 1 | Pickup — below threshold | 95% of setting | 55.945@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 2.00 s
27 | Undervoltage | Voltage | pickup+time | 2 | Pickup — above threshold | 105% of setting | 61.834@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
27 | Undervoltage | Voltage | pickup+time | 3 | Timing at 0.6× pickup | Step from nominal to the test level | 35.334@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 2.00 s | Definite time
27 | Undervoltage | Voltage | pickup+time | 4 | Below minimum operating voltage | Proves the element blocks rather than operating on a dead machine | 4.000@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | Element inhibited
59 | Overvoltage | Voltage | pickup+time | 1 | Pickup — above threshold | 105% of setting | 80.021@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 1.00 s
59 | Overvoltage | Voltage | pickup+time | 2 | Pickup — below threshold | 95% of setting | 72.400@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
59 | Overvoltage | Voltage | pickup+time | 3 | Timing at 1.25× pickup | Step from nominal to the test level | 95.263@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.00 s | Definite time
47 | Voltage unbalance / phase reversal | Quick CMC | points | 1 | Pickup — above threshold | V L1 dropped 22.86 V, giving V2 = 7.62 V | 46.419@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Operate after 2.0 s
47 | Voltage unbalance / phase reversal | Quick CMC | points | 2 | Pickup — below threshold | V L1 dropped 18.71 V, giving V2 = 6.24 V | 50.576@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | RESTRAIN | No operation
47 | Voltage unbalance / phase reversal | Quick CMC | points | 3 | Full phase reversal | Nominal balanced set with L2 and L3 exchanged — V2 equals the full phase voltage | 69.282@0.0 | 69.282@120.0 | 69.282@-120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | V2 = 69.28 V, far above any sensible setting
81 | Under / over frequency | Quick CMC | points | 1 | Pickup — past threshold | 0.100 Hz beyond the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.3 | yes | OPERATE | Operate after 0.30 s
81 | Under / over frequency | Quick CMC | points | 2 | Pickup — short of threshold | 0.100 Hz on the healthy side | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.5 | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 3 | Timing | Step from 60.0 Hz straight to 59.300 Hz | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.3 | yes | 0.300 s | Definite time
81 | Under / over frequency | Quick CMC | points | 4 | Below minimum voltage | Frequency past the setting but voltage under the 30 V supervision level | 24.000@0.0 | 24.000@-120.0 | 24.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.3 | yes | BLOCKED | Element inhibited
81R | Rate of change of frequency | Ramping | ramp | 1 | Rate above pickup | Ramp 60.00 → 57.00 Hz at 1.800 Hz/s · 1.67 s of travel | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Operate after 0.20 s of sustained rate
81R | Rate of change of frequency | Ramping | ramp | 2 | Rate below pickup | Ramp 60.00 → 57.00 Hz at 1.200 Hz/s · 2.50 s of travel | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | RESTRAIN | No operation
81R | Rate of change of frequency | Ramping | ramp | 3 | Well above pickup | Ramp 60.00 → 57.00 Hz at 4.500 Hz/s · 0.67 s of travel | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Operate after 0.20 s of sustained rate
25 | Synchrocheck | Synchronizer | points | 1 | In synchronism | All three differences well inside their limits | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz
25 | Synchrocheck | Synchronizer | points | 2 | Angle just inside limit | Angle at 80% of the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@8.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | CLOSE PERMITTED | Δθ 8.0°
25 | Synchrocheck | Synchronizer | points | 3 | Angle just outside limit | Angle at 120% of the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@12.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | BLOCKED | Δθ 12.0°
25 | Synchrocheck | Synchronizer | points | 4 | Voltage difference outside limit | Angle matched, magnitude offset past ΔV | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 63.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | BLOCKED | ΔV 6.00 V
25 | Synchrocheck | Synchronizer | points | 5 | Slip outside limit | Bus output run off frequency so the angle rotates | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | BLOCKED | Δf 0.060 Hz
25 | Synchrocheck | Synchronizer | points | 6 | Dead bus, live machine | Bus collapsed below the dead threshold | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled

## Channels
Function | Description | Group | TU module | Drive as | # | Test step | Channel | Magnitude | Unit | Angle deg | Hz | Note | Expected | Expected — detail | Verdict
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I A-L1 | 2.0918 | A | 0 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I A-L2 | 2.0918 | A | -120 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I A-L3 | 2.0918 | A | 120 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I B-L1 | 1.6316 | A | 180 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I B-L2 | 1.6316 | A | 60 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I B-L3 | 1.6316 | A | -60 | 60 |  | OPERATE | IT 0.500 pu · IN 0.390 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I A-L1 | 2.0918 | A | 0 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I A-L2 | 2.0918 | A | -120 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I A-L3 | 2.0918 | A | 120 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I B-L1 | 1.7153 | A | 180 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I B-L2 | 1.7153 | A | 60 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I B-L3 | 1.7153 | A | -60 | 60 |  | RESTRAIN | IT 0.500 pu · IN 0.410 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | I A-L1 | 4.1837 | A | 0 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | I A-L2 | 4.1837 | A | -120 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | I A-L3 | 4.1837 | A | 120 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | I B-L1 | 3.7235 | A | 180 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | I B-L2 | 3.7235 | A | 60 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 3 | Irest 1 pu — above slope | I B-L3 | 3.7235 | A | -60 | 60 |  | OPERATE | IT 1.000 pu · IN 0.890 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | I A-L1 | 4.1837 | A | 0 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | I A-L2 | 4.1837 | A | -120 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | I A-L3 | 4.1837 | A | 120 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | I B-L1 | 3.8072 | A | 180 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | I B-L2 | 3.8072 | A | 60 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 4 | Irest 1 pu — below slope | I B-L3 | 3.8072 | A | -60 | 60 |  | RESTRAIN | IT 1.000 pu · IN 0.910 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | I A-L1 | 12.5511 | A | 0 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | I A-L2 | 12.5511 | A | -120 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | I A-L3 | 12.5511 | A | 120 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | I B-L1 | 11.1705 | A | 180 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | I B-L2 | 11.1705 | A | 60 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 5 | Irest 3 pu — above slope | I B-L3 | 11.1705 | A | -60 | 60 |  | OPERATE | IT 3.000 pu · IN 2.670 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | I A-L1 | 12.5511 | A | 0 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | I A-L2 | 12.5511 | A | -120 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | I A-L3 | 12.5511 | A | 120 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | I B-L1 | 11.4215 | A | 180 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | I B-L2 | 11.4215 | A | 60 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 6 | Irest 3 pu — below slope | I B-L3 | 11.4215 | A | -60 | 60 |  | RESTRAIN | IT 3.000 pu · IN 2.730 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | I A-L1 | 29.2859 | A | 0 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | I A-L2 | 29.2859 | A | -120 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | I A-L3 | 29.2859 | A | 120 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | I B-L1 | 24.2236 | A | 180 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | I B-L2 | 24.2236 | A | 60 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 7 | Irest 7 pu — above slope | I B-L3 | 24.2236 | A | -60 | 60 |  | OPERATE | IT 7.000 pu · IN 5.790 pu | op
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | I A-L1 | 29.2859 | A | 0 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | I A-L2 | 29.2859 | A | -120 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | I A-L3 | 29.2859 | A | 120 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | I B-L1 | 25.144 | A | 180 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | I B-L2 | 25.144 | A | 60 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87G | Generator differential | Differential & ground | Differential | characteristic | 8 | Irest 7 pu — below slope | I B-L3 | 25.144 | A | -60 | 60 |  | RESTRAIN | IT 7.000 pu · IN 6.010 pu | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 1 | Sensitivity — above pickup | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate time 0.00 s | op
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 1 | Sensitivity — above pickup | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate time 0.00 s | op
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 1 | Sensitivity — above pickup | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate time 0.00 s | op
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 1 | Sensitivity — above pickup | I A-L1 | 0.55 | A | 0 | 60 | ground / neutral CT input | OPERATE | Operate time 0.00 s | op
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 2 | Sensitivity — below pickup | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Operate time 0.00 s | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 2 | Sensitivity — below pickup | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Operate time 0.00 s | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 2 | Sensitivity — below pickup | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Operate time 0.00 s | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 2 | Sensitivity — below pickup | I A-L1 | 0.45 | A | 0 | 60 | ground / neutral CT input | RESTRAIN | Operate time 0.00 s | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 3 | Through-fault stability | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation anywhere on the ramp | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 3 | Through-fault stability | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation anywhere on the ramp | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 3 | Through-fault stability | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation anywhere on the ramp | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 3 | Through-fault stability | I A-L1 | 20 | A | 0 | 60 | terminal phase L1 | RESTRAIN | No operation anywhere on the ramp | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 3 | Through-fault stability | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation anywhere on the ramp | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 3 | Through-fault stability | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation anywhere on the ramp | no
87GN | Restricted ground fault | Differential & ground | Quick CMC | points | 3 | Through-fault stability | I B-L1 | 500 | A | 180 | 60 | ground CT input, reversed polarity | RESTRAIN | No operation anywhere on the ramp | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 0.50 s | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 0.50 s | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 1 | Pickup — above threshold | V 4 | 5.5 | V | 0 | 60 | grounding transformer secondary | OPERATE | Operate after 0.50 s | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 1 | Pickup — above threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 2 | Pickup — below threshold | V 4 | 4.5 | V | 0 | 60 | grounding transformer secondary | RESTRAIN | No operation | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 2 | Pickup — below threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 3 | Fault 100% from neutral | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 3 | Fault 100% from neutral | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 3 | Fault 100% from neutral | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 3 | Fault 100% from neutral | V 4 | 239.923 | V | 0 | 60 | grounding transformer secondary | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 3 | Fault 100% from neutral | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 3 | Fault 100% from neutral | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 3 | Fault 100% from neutral | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 4 | Fault 50% from neutral | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 4 | Fault 50% from neutral | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 4 | Fault 50% from neutral | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 4 | Fault 50% from neutral | V 4 | 119.961 | V | 0 | 60 | grounding transformer secondary | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 4 | Fault 50% from neutral | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 4 | Fault 50% from neutral | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 4 | Fault 50% from neutral | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 5 | Fault 10% from neutral | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 5 | Fault 10% from neutral | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 5 | Fault 10% from neutral | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 5 | Fault 10% from neutral | V 4 | 23.992 | V | 0 | 60 | grounding transformer secondary | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 5 | Fault 10% from neutral | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 5 | Fault 10% from neutral | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 5 | Fault 10% from neutral | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 6 | Fault 5% from neutral | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 6 | Fault 5% from neutral | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 6 | Fault 5% from neutral | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 6 | Fault 5% from neutral | V 4 | 11.996 | V | 0 | 60 | grounding transformer secondary | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 6 | Fault 5% from neutral | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 6 | Fault 5% from neutral | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
59N | Stator ground — fundamental | Differential & ground | Quick CMC | points | 6 | Fault 5% from neutral | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Detected by 59N | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | V 4 | 0.55 | V | 0 | 180 | third harmonic at the neutral input | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | I A-L1 | 0.4184 | A | 0 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | I A-L2 | 0.4184 | A | -120 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | I A-L3 | 0.4184 | A | 120 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 1 | Above threshold — healthy | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | Element must not operate | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | V 4 | 0.45 | V | 0 | 180 | third harmonic at the neutral input | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | I A-L1 | 0.4184 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | I A-L2 | 0.4184 | A | -120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | I A-L3 | 0.4184 | A | 120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 2 | Below threshold — fault | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | V 4 | 0 | V | 0 | 180 | third harmonic at the neutral input | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | I A-L1 | 0.4184 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | I A-L2 | 0.4184 | A | -120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | I A-L3 | 0.4184 | A | 120 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 3 | Third harmonic removed | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.0 s | op
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | V 4 | 0 | V | 0 | 60 | third harmonic removed | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | I B-L1 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | I B-L2 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27TN | Stator ground — third harmonic | Differential & ground | Harmonics | points | 4 | Supervision withdrawn | I B-L3 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | V L1 | 51.75 | V | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | V L2 | 51.75 | V | -120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | V L3 | 51.75 | V | 120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | I A-L1 | 5 | A | 90 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | I A-L2 | 5 | A | -30 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | I A-L3 | 5 | A | -150 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 1 | Circle centre | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | V L1 | 13.662 | V | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | V L2 | 13.662 | V | -120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | V L3 | 13.662 | V | 120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | I A-L1 | 5 | A | 90 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | I A-L2 | 5 | A | -30 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | I A-L3 | 5 | A | -150 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 2 | Boundary top — inside | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | V L1 | 7.038 | V | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | V L2 | 7.038 | V | -120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | V L3 | 7.038 | V | 120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | I A-L1 | 5 | A | 90 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | I A-L2 | 5 | A | -30 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | I A-L3 | 5 | A | -150 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 3 | Boundary top — outside | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | V L1 | 89.838 | V | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | V L2 | 89.838 | V | -120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | V L3 | 89.838 | V | 120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | I A-L1 | 5 | A | 90 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | I A-L2 | 5 | A | -30 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | I A-L3 | 5 | A | -150 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 4 | Boundary bottom — inside | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | V L1 | 96.462 | V | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | V L2 | 96.462 | V | -120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | V L3 | 96.462 | V | 120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | I A-L1 | 5 | A | 90 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | I A-L2 | 5 | A | -30 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | I A-L3 | 5 | A | -150 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 5 | Boundary bottom — outside | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | V L1 | 64.255 | V | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | V L2 | 64.255 | V | -120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | V L3 | 64.255 | V | 120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | I A-L1 | 5 | A | 53.65 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | I A-L2 | 5 | A | -66.35 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | I A-L3 | 5 | A | 173.65 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 6 | Boundary right — inside | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | V L1 | 68.39 | V | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | V L2 | 68.39 | V | -120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | V L3 | 68.39 | V | 120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | I A-L1 | 5 | A | 49.17 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | I A-L2 | 5 | A | -70.83 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | I A-L3 | 5 | A | 169.17 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 7 | Boundary right — outside | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | V L1 | 64.255 | V | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | V L2 | 64.255 | V | -120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | V L3 | 64.255 | V | 120 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | I A-L1 | 5 | A | 126.35 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | I A-L2 | 5 | A | 6.35 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | I A-L3 | 5 | A | -113.65 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 8 | Boundary left — inside | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.10 s | op
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | V L1 | 68.39 | V | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | V L2 | 68.39 | V | -120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | V L3 | 68.39 | V | 120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | I A-L1 | 5 | A | 130.83 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | I A-L2 | 5 | A | 10.83 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | I A-L3 | 5 | A | -109.17 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 9 | Boundary left — outside | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | V L1 | 82.8 | V | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | V L2 | 82.8 | V | -120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | V L3 | 82.8 | V | 120 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | I A-L1 | 5 | A | -90 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | I A-L2 | 5 | A | 150 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | I A-L3 | 5 | A | 30 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
40 | Loss of excitation | Machine | Advanced Distance | shots | 10 | Normal excitation | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 1.1045 | A | 0 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Very long operate time at this level | op
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 0.9037 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | V L1 | 69.282 | V | 0 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | V L2 | 69.282 | V | -120 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | V L3 | 69.282 | V | 120 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | I A-L1 | 1.8827 | A | 0 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | I A-L2 | 0 | A | 0 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | I A-L3 | 0 | A | 0 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | I B-L1 | 0 | A | 0 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | I B-L2 | 0 | A | 0 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 3 | Timing at I2 = 0.15 pu | I B-L3 | 0 | A | 0 | 60 |  | 444.4 s | 7.41 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | V L1 | 69.282 | V | 0 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | V L2 | 69.282 | V | -120 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | V L3 | 69.282 | V | 120 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | I A-L1 | 2.5102 | A | 0 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | I A-L2 | 0 | A | 0 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | I A-L3 | 0 | A | 0 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | I B-L1 | 0 | A | 0 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | I B-L2 | 0 | A | 0 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 4 | Timing at I2 = 0.2 pu | I B-L3 | 0 | A | 0 | 60 |  | 250.0 s | 4.17 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | V L1 | 69.282 | V | 0 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | V L2 | 69.282 | V | -120 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | V L3 | 69.282 | V | 120 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | I A-L1 | 3.7653 | A | 0 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | I A-L2 | 0 | A | 0 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | I A-L3 | 0 | A | 0 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | I B-L1 | 0 | A | 0 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | I B-L2 | 0 | A | 0 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 5 | Timing at I2 = 0.3 pu | I B-L3 | 0 | A | 0 | 60 |  | 111.1 s | 1.85 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | V L1 | 69.282 | V | 0 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | V L2 | 69.282 | V | -120 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | V L3 | 69.282 | V | 120 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | I A-L1 | 6.2755 | A | 0 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | I A-L2 | 0 | A | 0 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | I A-L3 | 0 | A | 0 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | I B-L1 | 0 | A | 0 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | I B-L2 | 0 | A | 0 | 60 |  | 40.0 s | 0.67 minutes | nu
46 | Negative-sequence capability | Machine | Overcurrent | characteristic | 6 | Timing at I2 = 0.5 pu | I B-L3 | 0 | A | 0 | 60 |  | 40.0 s | 0.67 minutes | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | I A-L1 | 0.0427 | A | 180 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | I A-L2 | 0.0427 | A | 60 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | I A-L3 | 0.0427 | A | -60 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 1 | Above threshold — motoring | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Balanced 3φ · current at +180.0° · 1.0200 MW primary | op
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | I A-L1 | 0.0284 | A | 180 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | I A-L2 | 0.0284 | A | 60 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | I A-L3 | 0.0284 | A | -60 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 2 | Below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | Balanced 3φ · current at +180.0° · 0.6800 MW primary | no
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | I A-L1 | 0.0711 | A | 180 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | I A-L2 | 0.0711 | A | 60 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | I A-L3 | 0.0711 | A | -60 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
32 | Reverse / low forward power | Machine | Quick CMC | points | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 10.0 s | Balanced 3φ · current at +180.0° · 1.7000 MW primary | nu
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | V L1 | 69.282 | V | 90 | 60 | healthy phase, held at nominal | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | V L2 | 91.411 | V | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | V L3 | 91.411 | V | 180 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | I A-L2 | 5 | A | -85 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | I A-L3 | 5 | A | 95 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 1 | Reach at MTA — inside | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | V L1 | 69.282 | V | 90 | 60 | healthy phase, held at nominal | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | V L2 | 107.309 | V | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | V L3 | 107.309 | V | 180 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | I A-L2 | 5 | A | -85 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | I A-L3 | 5 | A | 95 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 2 | Reach at MTA — outside | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | V L1 | 69.282 | V | 90 | 60 | healthy phase, held at nominal | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | V L2 | 79.164 | V | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | V L3 | 79.164 | V | 180 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | I A-L2 | 5 | A | -115 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | I A-L3 | 5 | A | 65 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 3 | Reach at MTA +30° — inside | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | V L1 | 69.282 | V | 90 | 60 | healthy phase, held at nominal | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | V L2 | 92.932 | V | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | V L3 | 92.932 | V | 180 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | I A-L2 | 5 | A | -115 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | I A-L3 | 5 | A | 65 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 4 | Reach at MTA +30° — outside | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | V L1 | 69.282 | V | 90 | 60 | healthy phase, held at nominal | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | V L2 | 79.164 | V | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | V L3 | 79.164 | V | 180 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | I A-L2 | 5 | A | -55 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | I A-L3 | 5 | A | 125 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 5 | Reach at MTA −30° — inside | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 0.50 s | op
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | V L1 | 69.282 | V | 90 | 60 | healthy phase, held at nominal | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | V L2 | 92.932 | V | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | V L3 | 92.932 | V | 180 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | I A-L2 | 5 | A | -55 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | I A-L3 | 5 | A | 125 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
21 | Distance backup | Machine | Advanced Distance | shots | 6 | Reach at MTA −30° — outside | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | V L1 | 62.1 | V | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | V L2 | 62.1 | V | -120 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | V L3 | 62.1 | V | 120 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | I A-L1 | 5 | A | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | I A-L2 | 5 | A | -120 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | I A-L3 | 5 | A | 120 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | I B-L1 | 0 | A | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | I B-L2 | 0 | A | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 1 | Right of the right blinder | I B-L3 | 0 | A | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | V L1 | 37.26 | V | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | V L2 | 37.26 | V | -120 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | V L3 | 37.26 | V | 120 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | I A-L1 | 5 | A | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | I A-L2 | 5 | A | -120 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | I A-L3 | 5 | A | 120 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | I B-L1 | 0 | A | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | I B-L2 | 0 | A | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 2 | Inside the right blinder | I B-L3 | 0 | A | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | V L1 | 37.26 | V | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | V L2 | 37.26 | V | -120 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | V L3 | 37.26 | V | 120 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | I A-L1 | 5 | A | 180 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | I A-L2 | 5 | A | 60 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | I A-L3 | 5 | A | -60 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | I B-L1 | 0 | A | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | I B-L2 | 0 | A | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 3 | Inside the left blinder | I B-L3 | 0 | A | 0 | 60 |  | INSIDE | Inside the blinder pair | op
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | V L1 | 62.1 | V | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | V L2 | 62.1 | V | -120 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | V L3 | 62.1 | V | 120 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | I A-L1 | 5 | A | 180 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | I A-L2 | 5 | A | 60 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | I A-L3 | 5 | A | -60 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | I B-L1 | 0 | A | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | I B-L2 | 0 | A | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
78 | Out of step | Machine | Advanced Distance | shots | 4 | Left of the left blinder | I B-L3 | 0 | A | 0 | 60 |  | OUTSIDE | Outside the blinder pair | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | V L1 | 69.282 | V | 0 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | V L2 | 69.282 | V | -120 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | V L3 | 69.282 | V | 120 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | I A-L1 | 0 | A | 0 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | I A-L2 | 0 | A | 0 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | I A-L3 | 0 | A | 0 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | I B-L1 | 0 | A | 0 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | I B-L2 | 0 | A | 0 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 1 | Step 1 — machine on line, disarmed | I B-L3 | 0 | A | 0 | 60 |  | DISARMED | Arming flag must stay dropped | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | I A-L1 | 5 | A | -75 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | I A-L2 | 5 | A | 165 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | I A-L3 | 5 | A | 45 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | I B-L1 | 0 | A | 0 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | I B-L2 | 0 | A | 0 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 2 | Step 2 — current while disarmed | I B-L3 | 0 | A | 0 | 60 |  | NO TRIP | This is the step that catches a scheme armed by mistake | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | V L1 | 27.713 | V | 0 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | V L2 | 27.713 | V | -120 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | V L3 | 27.713 | V | 120 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | I A-L1 | 0 | A | 0 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | I A-L2 | 0 | A | 0 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | I A-L3 | 0 | A | 0 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | I B-L1 | 0 | A | 0 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | I B-L2 | 0 | A | 0 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 3 | Step 3 — machine off line, arming | I B-L3 | 0 | A | 0 | 60 |  | ARMS | Arming flag picks up after 5.0 s | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | V L1 | 27.713 | V | 0 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | V L2 | 27.713 | V | -120 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | V L3 | 27.713 | V | 120 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | I A-L1 | 2.25 | A | -75 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | I A-L2 | 2.25 | A | 165 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | I A-L3 | 2.25 | A | 45 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | I B-L1 | 0 | A | 0 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | I B-L2 | 0 | A | 0 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 4 | Step 4 — current below pickup | I B-L3 | 0 | A | 0 | 60 |  | NO TRIP | 90% of pickup | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | V L1 | 27.713 | V | 0 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | V L2 | 27.713 | V | -120 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | V L3 | 27.713 | V | 120 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | I A-L1 | 2.75 | A | -75 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | I A-L2 | 2.75 | A | 165 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | I A-L3 | 2.75 | A | 45 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | I B-L1 | 0 | A | 0 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | I B-L2 | 0 | A | 0 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 5 | Step 5 — current above pickup | I B-L3 | 0 | A | 0 | 60 |  | TRIP | Instantaneous, no intentional delay | op
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | I A-L1 | 5 | A | -75 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | I A-L2 | 5 | A | 165 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | I A-L3 | 5 | A | 45 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | I B-L1 | 0 | A | 0 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | I B-L2 | 0 | A | 0 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
50/27 | Inadvertent energization | Machine | State Sequencer | sequence (assemble from these steps) | 6 | Step 6 — disarm and re-apply | I B-L3 | 0 | A | 0 | 60 |  | NO TRIP | Proves the scheme disarms on restoration | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | I A-L1 | 7.875 | A | -75 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 1 | V = 1 ×VT — above pickup | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | I A-L1 | 7.125 | A | -75 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 2 | V = 1 ×VT — below pickup | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | V L1 | 69.282 | V | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | V L2 | 69.282 | V | -120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | V L3 | 69.282 | V | 120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | I A-L1 | 15 | A | -75 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | I A-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | I A-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | I B-L1 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | I B-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 3 | V = 1 ×VT — timing at 2× effective | I B-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | V L1 | 51.962 | V | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | V L2 | 51.962 | V | -120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | V L3 | 51.962 | V | 120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | I A-L1 | 5.9063 | A | -75 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 4 | V = 0.75 ×VT — above pickup | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | V L1 | 51.962 | V | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | V L2 | 51.962 | V | -120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | V L3 | 51.962 | V | 120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | I A-L1 | 5.3438 | A | -75 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 5 | V = 0.75 ×VT — below pickup | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | V L1 | 51.962 | V | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | V L2 | 51.962 | V | -120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | V L3 | 51.962 | V | 120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | I A-L1 | 11.25 | A | -75 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | I A-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | I A-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | I B-L1 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | I B-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 6 | V = 0.75 ×VT — timing at 2× effective | I B-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | V L1 | 34.641 | V | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | V L2 | 34.641 | V | -120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | V L3 | 34.641 | V | 120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | I A-L1 | 3.9375 | A | -75 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 7 | V = 0.5 ×VT — above pickup | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | V L1 | 34.641 | V | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | V L2 | 34.641 | V | -120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | V L3 | 34.641 | V | 120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | I A-L1 | 3.5625 | A | -75 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 8 | V = 0.5 ×VT — below pickup | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | V L1 | 34.641 | V | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | V L2 | 34.641 | V | -120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | V L3 | 34.641 | V | 120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | I A-L1 | 7.5 | A | -75 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | I A-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | I A-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | I B-L1 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | I B-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 9 | V = 0.5 ×VT — timing at 2× effective | I B-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | V L1 | 17.321 | V | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | V L2 | 17.321 | V | -120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | V L3 | 17.321 | V | 120 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | I A-L1 | 1.9688 | A | -75 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 10 | V = 0.25 ×VT — above pickup | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Curve runs from here | op
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | V L1 | 17.321 | V | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | V L2 | 17.321 | V | -120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | V L3 | 17.321 | V | 120 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | I A-L1 | 1.7813 | A | -75 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 11 | V = 0.25 ×VT — below pickup | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | V L1 | 17.321 | V | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | V L2 | 17.321 | V | -120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | V L3 | 17.321 | V | 120 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | I A-L1 | 3.75 | A | -75 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | I A-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | I A-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | I B-L1 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | I B-L2 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
51V | Voltage-restrained OC | Machine | Quick CMC | points | 12 | V = 0.25 ×VT — timing at 2× effective | I B-L3 | 0 | A | 0 | 60 |  | 1.406 s | Multiple is of the effective pickup, not the nominal one | nu
24 | Volts per hertz | Machine | Quick CMC | points | 1 | 60 Hz — above threshold | V L1 | 80.021 | V | 0 | 60 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 1 | 60 Hz — above threshold | V L2 | 80.021 | V | -120 | 60 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 1 | 60 Hz — above threshold | V L3 | 80.021 | V | 120 | 60 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 1 | 60 Hz — above threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 1 | 60 Hz — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 1 | 60 Hz — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 2 | 60 Hz — below threshold | V L1 | 72.4 | V | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 2 | 60 Hz — below threshold | V L2 | 72.4 | V | -120 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 2 | 60 Hz — below threshold | V L3 | 72.4 | V | 120 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 2 | 60 Hz — below threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 2 | 60 Hz — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 2 | 60 Hz — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 3 | 57 Hz — above threshold | V L1 | 76.02 | V | 0 | 57 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 3 | 57 Hz — above threshold | V L2 | 76.02 | V | -120 | 57 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 3 | 57 Hz — above threshold | V L3 | 76.02 | V | 120 | 57 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 3 | 57 Hz — above threshold | I A-L1 | 0 | A | 0 | 57 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 3 | 57 Hz — above threshold | I A-L2 | 0 | A | 0 | 57 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 3 | 57 Hz — above threshold | I A-L3 | 0 | A | 0 | 57 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 4 | 57 Hz — below threshold | V L1 | 68.78 | V | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 4 | 57 Hz — below threshold | V L2 | 68.78 | V | -120 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 4 | 57 Hz — below threshold | V L3 | 68.78 | V | 120 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 4 | 57 Hz — below threshold | I A-L1 | 0 | A | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 4 | 57 Hz — below threshold | I A-L2 | 0 | A | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 4 | 57 Hz — below threshold | I A-L3 | 0 | A | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 5 | 54 Hz — above threshold | V L1 | 72.019 | V | 0 | 54 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 5 | 54 Hz — above threshold | V L2 | 72.019 | V | -120 | 54 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 5 | 54 Hz — above threshold | V L3 | 72.019 | V | 120 | 54 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 5 | 54 Hz — above threshold | I A-L1 | 0 | A | 0 | 54 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 5 | 54 Hz — above threshold | I A-L2 | 0 | A | 0 | 54 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 5 | 54 Hz — above threshold | I A-L3 | 0 | A | 0 | 54 |  | OPERATE | Operate after 20.00 s | op
24 | Volts per hertz | Machine | Quick CMC | points | 6 | 54 Hz — below threshold | V L1 | 65.16 | V | 0 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 6 | 54 Hz — below threshold | V L2 | 65.16 | V | -120 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 6 | 54 Hz — below threshold | V L3 | 65.16 | V | 120 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 6 | 54 Hz — below threshold | I A-L1 | 0 | A | 0 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 6 | 54 Hz — below threshold | I A-L2 | 0 | A | 0 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 6 | 54 Hz — below threshold | I A-L3 | 0 | A | 0 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Machine | Quick CMC | points | 7 | Timing at 1.2× pickup | V L1 | 91.452 | V | 0 | 60 |  | 5.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 7 | Timing at 1.2× pickup | V L2 | 91.452 | V | -120 | 60 |  | 5.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 7 | Timing at 1.2× pickup | V L3 | 91.452 | V | 120 | 60 |  | 5.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 7 | Timing at 1.2× pickup | I A-L1 | 0 | A | 0 | 60 |  | 5.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 7 | Timing at 1.2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 5.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 7 | Timing at 1.2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 5.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 8 | Timing at 1.5× pickup | V L1 | 114.315 | V | 0 | 60 |  | 2.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 8 | Timing at 1.5× pickup | V L2 | 114.315 | V | -120 | 60 |  | 2.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 8 | Timing at 1.5× pickup | V L3 | 114.315 | V | 120 | 60 |  | 2.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 8 | Timing at 1.5× pickup | I A-L1 | 0 | A | 0 | 60 |  | 2.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 8 | Timing at 1.5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 2.00 s | From the inverse characteristic | nu
24 | Volts per hertz | Machine | Quick CMC | points | 8 | Timing at 1.5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 2.00 s | From the inverse characteristic | nu
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | I A-L1 | 2.0918 | A | 23.19 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | I A-L2 | 2.0918 | A | -96.81 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | I A-L3 | 2.0918 | A | 143.19 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 1 | Past the limit | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | pf = 0.919 leading | op
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | I A-L1 | 2.0918 | A | 13.19 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | I A-L2 | 2.0918 | A | -106.81 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | I A-L3 | 2.0918 | A | 133.19 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 2 | Short of the limit | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | pf = 0.974 leading | no
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | I A-L1 | 2.0918 | A | 90 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | I A-L2 | 2.0918 | A | -30 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | I A-L3 | 2.0918 | A | -150 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 3 | Full VAR, no watts | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | pf = 0.000 leading | op
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | I A-L1 | 0.6694 | A | 23.19 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | I A-L2 | 0.6694 | A | -96.81 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | I A-L3 | 0.6694 | A | 143.19 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | I B-L1 | 0 | A | 0 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | I B-L2 | 0 | A | 0 | 60 |  | BLOCKED | pf = 0.919 leading | no
55 | Power factor | Machine | Quick CMC | points | 4 | Below minimum current | I B-L3 | 0 | A | 0 | 60 |  | BLOCKED | pf = 0.919 leading | no
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | I A-L1 | 5.2715 | A | -25 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 1 | Operate at 1.2× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 602.6 s | 10.04 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | I A-L1 | 6.5893 | A | -25 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 2 | Operate at 1.5× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 260.4 s | 4.34 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | I A-L1 | 8.7858 | A | -25 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 3 | Operate at 2× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 117.8 s | 1.96 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | I A-L1 | 13.1786 | A | -25 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 46.0 s | 0.77 minutes | nu
49 | Stator thermal overload | Machine | Overcurrent | characteristic | 4 | Operate at 3× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 46.0 s | 0.77 minutes | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L1 | 21 | A | -75 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L1 | 19 | A | -75 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L1 | 40 | A | -75 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 5.775 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 5.225 | A | -75 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L1 | 11 | A | -75 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L1 | 16.5 | A | -75 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L1 | 27.5 | A | -75 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L1 | 2.625 | A | -75 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L1 | 2.375 | A | -75 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L1 | 5 | A | -75 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 1.05 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 0.95 | A | -75 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L1 | 2 | A | -75 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L1 | 3 | A | -75 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L1 | 5 | A | -75 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L1 | 2.625 | A | -75 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L1 | 2.375 | A | -75 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L1 | 5 | A | -75 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 1.05 | A | -75 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — let the curve run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 0.95 | A | -75 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L1 | 2 | A | -75 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.406 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L1 | 3 | A | -75 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.588 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L1 | 5 | A | -75 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.262 s | Predicted from the curve equation | nu
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | I A-L1 | 11 | A | -45 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | I A-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | I A-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | I B-L1 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | I B-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 1 | Forward maximum torque | I B-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | I A-L1 | 11 | A | 135 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | I A-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | I A-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | I B-L1 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | I B-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 2 | Reverse maximum torque | I B-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | I A-L1 | 11 | A | 40 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | I A-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | I A-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | I B-L1 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | I B-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 3 | Boundary, leading side (inside) | I B-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | I A-L1 | 11 | A | 50 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | I A-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | I A-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | I B-L1 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | I B-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 4 | Boundary, leading side (outside) | I B-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | I A-L1 | 11 | A | -130 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | I A-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | I A-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | I B-L1 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | I B-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 5 | Boundary, lagging side (inside) | I B-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup | op
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | I A-L1 | 11 | A | -140 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | I A-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | I A-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | I B-L1 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | I B-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
67 | Directional supervision | Overcurrent | Ramping | points | 6 | Boundary, lagging side (outside) | I B-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | V L1 | 55.945 | V | 0 | 60 | depressed phase | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | V L1 | 61.834 | V | 0 | 60 | depressed phase | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | V L1 | 35.334 | V | 0 | 60 | depressed phase | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | V L2 | 69.282 | V | -120 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | V L3 | 69.282 | V | 120 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | I A-L1 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | I A-L2 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | I A-L3 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | I B-L1 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | I B-L2 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.6× pickup | I B-L3 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | V L1 | 4 | V | 0 | 60 | depressed phase | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I B-L1 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I B-L2 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I B-L3 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | V L1 | 80.021 | V | 0 | 60 | raised phase | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | V L1 | 72.4 | V | 0 | 60 | raised phase | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | V L1 | 95.263 | V | 0 | 60 | raised phase | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | I A-L1 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.25× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | V L1 | 46.419 | V | 0 | 60 | depressed by 22.86 V | OPERATE | Operate after 2.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 2.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 2.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.0 s | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | V L1 | 50.576 | V | 0 | 60 | depressed by 18.71 V | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | V2 = 69.28 V, far above any sensible setting | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal | V L2 | 69.282 | V | 120 | 60 |  | OPERATE | V2 = 69.28 V, far above any sensible setting | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal | V L3 | 69.282 | V | -120 | 60 |  | OPERATE | V2 = 69.28 V, far above any sensible setting | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | V2 = 69.28 V, far above any sensible setting | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | V2 = 69.28 V, far above any sensible setting | op
47 | Voltage unbalance / phase reversal | Voltage & frequency | Quick CMC | points | 3 | Full phase reversal | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | V2 = 69.28 V, far above any sensible setting | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | V L1 | 69.282 | V | 0 | 59.3 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | V L2 | 69.282 | V | -120 | 59.3 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | V L3 | 69.282 | V | 120 | 59.3 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | I A-L1 | 0 | A | 0 | 59.3 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | I A-L2 | 0 | A | 0 | 59.3 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | I A-L3 | 0 | A | 0 | 59.3 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | V L1 | 69.282 | V | 0 | 59.5 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | V L2 | 69.282 | V | -120 | 59.5 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | V L3 | 69.282 | V | 120 | 59.5 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | I A-L1 | 0 | A | 0 | 59.5 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | I A-L2 | 0 | A | 0 | 59.5 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | I A-L3 | 0 | A | 0 | 59.5 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | V L1 | 69.282 | V | 0 | 59.3 |  | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | V L2 | 69.282 | V | -120 | 59.3 |  | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | V L3 | 69.282 | V | 120 | 59.3 |  | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | I A-L1 | 0 | A | 0 | 59.3 |  | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | I A-L2 | 0 | A | 0 | 59.3 |  | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | I A-L3 | 0 | A | 0 | 59.3 |  | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | V L1 | 24 | V | 0 | 59.3 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | V L2 | 24 | V | -120 | 59.3 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | V L3 | 24 | V | 120 | 59.3 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | I A-L1 | 0 | A | 0 | 59.3 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | I A-L2 | 0 | A | 0 | 59.3 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | I A-L3 | 0 | A | 0 | 59.3 |  | BLOCKED | Element inhibited | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup | V L1 | 69.282 | V | 0 | 60 | ramp to 57.00 Hz over 1.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup | V L2 | 69.282 | V | -120 | 60 | ramp to 57.00 Hz over 1.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup | V L3 | 69.282 | V | 120 | 60 | ramp to 57.00 Hz over 1.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup | I A-L1 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 1.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup | I A-L2 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 1.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 1 | Rate above pickup | I A-L3 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 1.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup | V L1 | 69.282 | V | 0 | 60 | ramp to 57.00 Hz over 2.50 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup | V L2 | 69.282 | V | -120 | 60 | ramp to 57.00 Hz over 2.50 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup | V L3 | 69.282 | V | 120 | 60 | ramp to 57.00 Hz over 2.50 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup | I A-L1 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 2.50 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup | I A-L2 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 2.50 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 2 | Rate below pickup | I A-L3 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 2.50 s | RESTRAIN | No operation | no
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup | V L1 | 69.282 | V | 0 | 60 | ramp to 57.00 Hz over 0.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup | V L2 | 69.282 | V | -120 | 60 | ramp to 57.00 Hz over 0.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup | V L3 | 69.282 | V | 120 | 60 | ramp to 57.00 Hz over 0.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup | I A-L1 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 0.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup | I A-L2 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 0.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
81R | Rate of change of frequency | Voltage & frequency | Ramping | ramp | 3 | Well above pickup | I A-L3 | 0 | A | 0 | 60 | ramp to 57.00 Hz over 0.67 s | OPERATE | Operate after 0.20 s of sustained rate | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V L1 | 69.282 | V | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V L2 | 69.282 | V | -120 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V L3 | 69.282 | V | 120 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V 4 | 69.282 | V | 0 | 60 | running bus | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | I A-L1 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | I A-L2 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | I A-L3 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V L1 | 69.282 | V | 0 | 60 |  | CLOSE PERMITTED | Δθ 8.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V L2 | 69.282 | V | -120 | 60 |  | CLOSE PERMITTED | Δθ 8.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V L3 | 69.282 | V | 120 | 60 |  | CLOSE PERMITTED | Δθ 8.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V 4 | 69.282 | V | 8 | 60 | running bus | CLOSE PERMITTED | Δθ 8.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | I A-L1 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 8.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | I A-L2 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 8.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | I A-L3 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 8.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Δθ 12.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Δθ 12.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Δθ 12.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V 4 | 69.282 | V | 12 | 60 | running bus | BLOCKED | Δθ 12.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 12.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 12.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 12.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | ΔV 6.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | ΔV 6.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | ΔV 6.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V 4 | 63.282 | V | 0 | 60 | running bus | BLOCKED | ΔV 6.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 6.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 6.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 6.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V 4 | 69.282 | V | 0 | 60.06 | running bus — 60.060 Hz | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.060 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead bus, live machine | V L1 | 69.282 | V | 0 | 60 |  | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead bus, live machine | V L2 | 69.282 | V | -120 | 60 |  | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead bus, live machine | V L3 | 69.282 | V | 120 | 60 |  | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead bus, live machine | V 4 | 10 | V | 0 | 60 | running bus | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead bus, live machine | I A-L1 | 0 | A | 0 | 60 |  | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead bus, live machine | I A-L2 | 0 | A | 0 | 60 |  | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead bus, live machine | I A-L3 | 0 | A | 0 | 60 |  | PER DEAD-BUS LOGIC | Depends on the dead/live scheme enabled | nu

## Build guide
Building the 889 OCC in Test Universe
Assembles `889-GEN-steps.csv` and `889-GEN-channels.csv` into one Test Universe document —
27 elements, 137 steps. Build it once, save it as a template, and the next machine is a
re-point of the test object.
Values below are for the tool's **sample** machine: 100 MVA, 13.8 kV, 0.85 pf, 60 Hz,
two-pole, Xd 1.8 / X'd 0.25 / X"d 0.18 / X2 0.20 pu, terminal and neutral CTs 5000:5,
ground CT 200:5, VT 13800:120 wye, neutral grounding transformer 7970:240,
high-resistance grounded. Enter your real machine in `889.html`, re-run the generator,
and every number below moves. The header comment in each CSV records which configuration
produced it.
---
1 · Read section 7 first
A generator plan has an amplifier problem that a feeder plan does not, and it decides how
you build the document. Two elements in this plan cannot share a hardware configuration
with the rest. Settle that before you spend an hour assembling modules.
2 · Test object
¦ Field ¦ Sample value ¦ Where it comes from ¦
¦-------¦--------------¦---------------------¦
¦ Nominal voltage, secondary ¦ 120 V L–L (69.282 V L–N) ¦ VT 13800 : 120 ¦
¦ Nominal current, secondary ¦ 5 A ¦ CT 5000 : 5 ¦
¦ VT ratio ¦ 115 : 1 ¦ ¦
¦ CT ratio, terminal and neutral ¦ 1000 : 1 ¦ both ends of the machine ¦
¦ CT ratio, ground ¦ 40 : 1 ¦ 200 : 5 ¦
¦ NGT ratio ¦ 33.2 : 1 ¦ 7970 : 240 ¦
¦ Nominal frequency ¦ 60 Hz ¦ ¦
¦ Rated stator current ¦ 4183.7 A primary = 4.1837 A secondary ¦ `MVA / (√3 · kV)` ¦
¦ Base impedance, secondary ¦ 16.56 Ω ¦ `Zbp · CTR / VTR` ¦
**Rated stator current is the unit everything else is quoted in.** The differential, the
impedance elements and the capability curve are all in per unit of it, and 1 pu is
4.1837 A secondary. Get that one number wrong and the whole plan is wrong by the same
factor while still looking sensible.
Two derived machine impedances are worth writing on the test object as reference values
even though Test Universe has no field for them — they are what the loss-of-excitation
characteristic is checked against:
¦ Quantity ¦ Sample value ¦
¦---¦---¦
¦ X'd / 2 ¦ 2.07 Ω secondary ¦
¦ Xd ¦ 29.81 Ω secondary ¦
A zone 1 offset far from the first, or a zone 2 diameter far from the second, means the
setting was not derived from this machine.
3 · Hardware configuration
Two configurations, not one. See §7 for why.
**Configuration A — differential, 6 × 12.5 A.** Two current triples: `I A-*` is the
terminal end, `I B-*` the neutral end. Used by 87G and the 87GN stability point. Nothing
else in the plan needs a second triple.
**Configuration B — everything else, 3 × 32 A.** One triple, and the headroom that the
overcurrent elements need.
Voltage in both: three phases plus **V 4**, and V 4 does three different jobs across the
plan. It is not one connection:
¦ Used by ¦ V 4 carries ¦ Range in the plan ¦
¦---¦---¦---¦
¦ 59N ¦ Grounding-transformer secondary ¦ up to 239.9 V ¦
¦ 27TN ¦ Third harmonic at the neutral input ¦ 180 Hz ¦
¦ 25 ¦ Line side, independent frequency ¦ 60.06 Hz for the slip case ¦
Declare V 4 as an independent generator, not a copy of V L1 — the synchrocheck slip test
and the third-harmonic test both need it running at its own frequency. And note the
239.9 V figure: it is inside the 300 V channel limit, but only just, and a machine with a
lower NGT ratio will exceed it.
Binary I/O
¦ CMC ¦ Direction ¦ To / from the relay ¦
¦-----¦-----------¦---------------------¦
¦ Bin. in 1 ¦ in ¦ Trip / 86 lockout — the timing reference for every operate time ¦
¦ Bin. in 2 ¦ in ¦ Close permissive — 25 ¦
¦ Bin. in 3 ¦ in ¦ Alarm, on the elements that alarm before they trip ¦
¦ Bin. out 1 ¦ out ¦ 52a generator breaker ¦
¦ Bin. out 2 ¦ out ¦ 52b generator breaker ¦
¦ Bin. out 3 ¦ out ¦ Field breaker auxiliary, where 40 or 50/27 uses it ¦
The 52a/52b pair is what makes 50/27 testable at all — the scheme arms on a machine at
standstill with the breaker open and disarms when it closes, so the position contacts are
the input the whole sequence turns on.
4 · Module map
Filter `889-GEN-steps.csv` on `TU_Module`. This order puts the single-triple work first,
so you build every module in configuration B and change the amplifier arrangement once,
at the end, rather than twice.
¦ Order ¦ Module ¦ Elements ¦ Steps ¦
¦------:¦--------¦----------¦------:¦
¦ 1 ¦ Overcurrent — pickup + time ¦ 50P, 50G, 50N ¦ 9 ¦
¦ 2 ¦ Overcurrent — characteristic ¦ 46, 49, 51P, 51G, 51N ¦ 25 ¦
¦ 3 ¦ Voltage ¦ 27, 59 ¦ 7 ¦
¦ 4 ¦ Quick CMC ¦ 87GN, 59N, 32, 51V, 24, 55, 47, 81 ¦ 43 ¦
¦ 5 ¦ Harmonics ¦ 27TN ¦ 4 ¦
¦ 6 ¦ Ramping ¦ 67 (6 points), 81R (3 ramps) ¦ 9 ¦
¦ 7 ¦ Synchronizer ¦ 25 ¦ 6 ¦
¦ 8 ¦ Advanced Distance ¦ 40, 21, 78 ¦ 20 ¦
¦ 9 ¦ State Sequencer ¦ 50/27 (assembled from 6 steps) ¦ 6 ¦
¦ 10 ¦ Differential ¦ 87G ¦ 8 ¦
5 · Advanced Distance — three elements, three different jobs
All three place the device somewhere on the R–X plane, and it is easy to build them as
one module and then misread the results.
**40 loss of excitation.** Two offset mho circles, entered as shots. The `WhatIsApplied`
column gives the impedance. Undervoltage supervision at 0.80 × VT (55.4 V) has to stay
satisfied throughout, so the tool holds current and lets the terminal voltage follow the
impedance rather than the other way round. On losing field the machine draws VARs from
the system and the apparent impedance swings from the first quadrant into the fourth —
if your points are landing in the first quadrant, the characteristic is entered inverted.
**21 distance backup.** Phase-to-phase loop, reach 19.87 Ω secondary at 85°, no k0. Off
the characteristic angle the circle closes in by the cosine of the offset: at ±30° the
boundary is 86.6 % of the reach, not the reach. Points placed at the reach off-angle will
fail and the element will be fine.
**78 out of step.** The four impedances only locate the blinders. The discrimination is
the **transit time** between them, which means a sequence, and the direction of travel
matters — right to left is a pole slip, the same impedances in another order are not. The
static points in this plan sit at X = 0; real swings cross nearer the electrical centre,
so raise the locus height in the tool's test options if the relay is fussy about it.
6 · Stator ground — 59N and 27TN are one scheme
Do not test them separately and sign them off separately.
59N covers the winding from the terminals down. A solid terminal fault puts 239.9 V on
V 4 and the 5.00 V pickup leaves the bottom **2.1 %** of the winding uncovered. That blind
zone is exactly what 27TN exists for, so a 59N pass on its own does not mean the stator is
protected.
27TN is the one element on the relay where **removing** a quantity makes it trip. Build
its four steps so the third harmonic starts healthy at 180 Hz and steps down, and keep the
forward-power and positive-sequence voltage supervision satisfied throughout — without
them nothing happens no matter what you do to the neutral input.
The 27TN pickup is normally set from the machine's own measured third-harmonic profile at
several load points, not from a calculation. A bench-verified threshold is a bench-verified
threshold; it is not evidence that the setting suits this machine.
7 · Before you inject — the amplifier conflict
This is the section to read before building anything.
**87G needs two triples, which caps the current at 12.5 A per channel.** One per unit is
4.1837 A, so the highest restraint the 6 × 12.5 A arrangement can reach is
12.5 / 4.1837 = **2.99 pu**. The sample plan's restraint points are 0.5, 1.0, 3.0 and 7.0 pu:
¦ Restraint point ¦ Terminal-end current ¦ 6 × 12.5 A ¦
¦---¦---:¦---¦
¦ 0.50 pu ¦ 2.0918 A ¦ fine ¦
¦ 1.00 pu ¦ 4.1837 A ¦ fine ¦
¦ 3.00 pu ¦ 12.5511 A ¦ 0.4 % over the limit — it will clip ¦
¦ 7.00 pu ¦ 29.2859 A ¦ far out of reach ¦
Three ways out, in order of preference: drop the restraint points to something the
amplifier can reach and say on the record that the slope was proved over 0.5–2.9 pu;
add a second amplifier (a CMS 356 gives you 6 × 32 A and every point becomes reachable);
or prove the slope on the bench at reduced currents and the stability point at rated. Do
not raise the numbers and hope.
**50P cannot be tested in the differential configuration at all.** Its pickup is 4 × CT,
which is 20.000 A secondary — already past 12.5 A — and the timing shot at 2 × pickup is
**40.000 A**. In 3 × 32 A the pickup is reachable and the timing shot is not. The 40 A shot
needs the **1 × 64 A** arrangement, which parallels the three current outputs into a single
phase. That is a third hardware configuration and one shot, so run it deliberately at the
end of the day rather than discovering it mid-module.
**87GN has the same problem in miniature.** Its through-fault stability step drives the
phase and ground inputs in opposition at 20.000 A, so it needs the second triple and it is
over the 12.5 A cap. Run it at a reduced through current and record the level used — the
polarity finding it exists for does not depend on the magnitude, and a reversed CT fails
it just as clearly at 10 A.
**Everything else sits inside 3 × 32 A with room to spare.** The largest current outside
87G, 87GN and 50P is 27.5 A, on the 51P timing shot at 5 × pickup. Four more steps — one
on 49, one on 51V and two on 51P — sit between 12.5 and 32 A, which is another reason to
build the whole document in configuration B and change the amplifier once, at the end.
8 · After the first build
Save as a template with the test object detached. The module structure, the binary map,
the V 4 re-patching and the amplifier conflict do not change between machines — only the
numbers do, and those come out of the generator.
Two things this plan deliberately will not do: it will not let a 59N pass stand as
evidence that the whole stator is protected, and it will not pretend the differential
slope was tested at a restraint the amplifier could not produce.