## Start here
845-VEC — Multilin 845 transformer protection
How to use this workbook
Fill in | Only the two shaded columns on each test sheet: MEASURED and PASS / FAIL. Everything else is calculated and should not be edited by hand.
Example row | MEASURED "1.432 s", PASS / FAIL "PASS". Use the same unit the Expected column uses, so the two can be compared without conversion.
Untested steps | Record them as NOT TESTED with a reason. A blank result reads as work not yet done; it must never be left blank on a completed record.
If a setting changes | Do not edit numbers here. Change it in the relay tool, re-run the generator, and rebuild this workbook — that is what keeps the injected values and the calculations from drifting apart.
Where these values come from
Plan | 845-VEC — Multilin 845 transformer protection
Generated | generated 2026-09-15 01:39 from src/845-vec.html
Configuration | mva=20; mva2=26.7; mva3=33.3; mvaBase=onan; kv1=115; kv2=13.8; freq=60; rot=ABC; w1c=D; w2c=YN; clk=1; z=8.5; xr=12; oltcW=1; oltcHi=10; oltcLo=10; oltcN=16; oltcPos=0; gnd1=none; gnd1v=0; gnd2=ngrA; gnd2v=400; ct1p=150; ct1s=5; ct1c=wye; ct2p=1200; ct2s=5; ct2c=wye; ctgp=200; ctgs=5; refw=2; vtp=13800; vts=120; vtc=wye; vtw=2; cmc=6x; imax=12.5; vmax=300
Conventions | All quantities are SECONDARY at the relay terminals. Angles in degrees, CCW positive, V L1 = 0.
Sample data | Values shown are for the tool's sample configuration — re-generate after entering real station data.
Record identification
Station
Feeder / plant item
Device serial
Firmware
Setting file revision
Test set serial
Tested by
Date
Witnessed by
Sheets in this workbook
Test steps | 91 test steps — the record. Fill in MEASURED and PASS / FAIL.
Channels | 743 rows — one per channel per step, for pasting into a Test Universe module table.
Build guide | How to assemble this plan in Test Universe, and the thing about this relay most likely to be got wrong.
Progress
Total steps
Results entered
Passed
Failed
Not tested
Outstanding
Counts refer to the first test sheet only.

## Test steps
Function | Description | TU module | Drive as | # | Test step | What is applied | V L1 | V L2 | V L3 | V 4 | I L1 | I L2 | I L3 | I B-L1 | I B-L2 | I B-L3 | Hz | Reachable | Expected | Expected — detail | MEASURED | PASS / FAIL
87T | Percent differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | Idiff required 0.200 pu · applied 0.220 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.6735@0.0 | 1.6735@-120.0 | 1.6735@120.0 | 0.9762@150.0 | 0.9762@30.0 | 0.9762@-90.0 | 60 | yes | OPERATE | IW1 0.500 pu · IW2 0.280 pu
87T | Percent differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | Idiff required 0.200 pu · applied 0.180 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.6735@0.0 | 1.6735@-120.0 | 1.6735@120.0 | 1.1157@150.0 | 1.1157@30.0 | 1.1157@-90.0 | 60 | yes | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu
87T | Percent differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | Idiff required 0.375 pu · applied 0.413 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0204@0.0 | 5.0204@-120.0 | 5.0204@120.0 | 3.7915@150.0 | 3.7915@30.0 | 3.7915@-90.0 | 60 | yes | OPERATE | IW1 1.500 pu · IW2 1.087 pu
87T | Percent differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | Idiff required 0.375 pu · applied 0.338 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0204@0.0 | 5.0204@-120.0 | 5.0204@120.0 | 4.0530@150.0 | 4.0530@30.0 | 4.0530@-90.0 | 60 | yes | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu
87T | Percent differential | Differential | characteristic | 5 | Irest 3 pu — above slope | Idiff required 0.750 pu · applied 0.825 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 10.0409@0.0 | 10.0409@-120.0 | 10.0409@120.0 | 7.5830@150.0 | 7.5830@30.0 | 7.5830@-90.0 | 60 | yes | OPERATE | IW1 3.000 pu · IW2 2.175 pu
87T | Percent differential | Differential | characteristic | 6 | Irest 3 pu — below slope | Idiff required 0.750 pu · applied 0.675 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 10.0409@0.0 | 10.0409@-120.0 | 10.0409@120.0 | 8.1059@150.0 | 8.1059@30.0 | 8.1059@-90.0 | 60 | yes | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu
87T | Percent differential | Differential | characteristic | 7 | Irest 7 pu — above slope | Idiff required 2.100 pu · applied 2.310 pu (+10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 23.4287@0.0 | 23.4287@-120.0 | 23.4287@120.0 | 16.3513@150.0 | 16.3513@30.0 | 16.3513@-90.0 | 60 | yes | OPERATE | IW1 7.000 pu · IW2 4.690 pu
87T | Percent differential | Differential | characteristic | 8 | Irest 7 pu — below slope | Idiff required 2.100 pu · applied 1.890 pu (−10%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 23.4287@0.0 | 23.4287@-120.0 | 23.4287@120.0 | 17.8156@150.0 | 17.8156@30.0 | 17.8156@-90.0 | 60 | yes | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu
87T-H | Harmonic inhibit | Harmonics | points | 1 | 2nd — inrush — above threshold | Harmonic content 22.0% of fundamental (setting 20%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.3470@0.0 | [5 empty] | 60 | yes | RESTRAIN | Differential 1.00 pu present throughout
87T-H | Harmonic inhibit | Harmonics | points | 2 | 2nd — inrush — below threshold | Harmonic content 18.0% of fundamental (setting 20%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.3470@0.0 | [5 empty] | 60 | yes | OPERATE | Differential 1.00 pu present throughout
87T-H | Harmonic inhibit | Harmonics | points | 3 | 5th — overexcitation — above threshold | Harmonic content 33.0% of fundamental (setting 30%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.3470@0.0 | [5 empty] | 60 | yes | RESTRAIN | Differential 1.00 pu present throughout
87T-H | Harmonic inhibit | Harmonics | points | 4 | 5th — overexcitation — below threshold | Harmonic content 27.0% of fundamental (setting 30%) | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.3470@0.0 | [5 empty] | 60 | yes | OPERATE | Differential 1.00 pu present throughout
87G | Restricted ground fault | Differential | characteristic | 1 | Sensitivity — above pickup | Ground CT input only, phase CTs at zero. Applied 0.110 ×CT. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.5500@0.0 | [5 empty] | 60 | yes | OPERATE | Operate time 0.00 s
87G | Restricted ground fault | Differential | characteristic | 2 | Sensitivity — below pickup | Ground CT input only, phase CTs at zero. Applied 0.090 ×CT. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.4500@0.0 | [5 empty] | 60 | yes | RESTRAIN | Operate time 0.00 s
87G | Restricted ground fault | Differential | characteristic | 3 | Through-fault stability | Phase L1 and ground input driven in opposition at 4 ×CT — an external ground fault. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 20.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 120.0000@180.0 |  |  | 60 | yes | RESTRAIN | No operation at any point of the ramp
50P | Phase instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 42.000 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 42.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50P | Phase instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 38.000 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 38.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50P | Phase instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2× pickup | Step from prefault zero straight to the test value | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 80.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.050 s | Measured from application of current to trip contact
51P | Phase time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 6.300 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.3000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — allow the curve to run out
51P | Phase time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 5.700 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.7000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51P | Phase time OC | Overcurrent | characteristic | 3 | Timing at 2× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.428 s | Predicted from the curve equation
51P | Phase time OC | Overcurrent | characteristic | 4 | Timing at 3× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 18.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.547 s | Predicted from the curve equation
51P | Phase time OC | Overcurrent | characteristic | 5 | Timing at 5× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 30.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.195 s | Predicted from the curve equation
50G | Ground instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 2.625 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.6250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50G | Ground instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 2.375 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.3750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50G | Ground instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2× pickup | Step from prefault zero straight to the test value | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.050 s | Measured from application of current to trip contact
51G | Ground time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.050 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.0500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — allow the curve to run out
51G | Ground time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 0.950 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.9500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51G | Ground time OC | Overcurrent | characteristic | 3 | Timing at 2× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.428 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 4 | Timing at 3× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.547 s | Predicted from the curve equation
51G | Ground time OC | Overcurrent | characteristic | 5 | Timing at 5× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 5.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.195 s | Predicted from the curve equation
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 3.150 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.1500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 2.850 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.8500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50N | Neutral instantaneous OC | Overcurrent | pickup+time | 3 | Timing at 2× pickup | Step from prefault zero straight to the test value | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.050 s | Measured from application of current to trip contact
51N | Neutral time OC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.313 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.3125@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — allow the curve to run out
51N | Neutral time OC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 1.188 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.1875@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
51N | Neutral time OC | Overcurrent | characteristic | 3 | Timing at 2× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.5000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.428 s | Predicted from the curve equation
51N | Neutral time OC | Overcurrent | characteristic | 4 | Timing at 3× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.7500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.547 s | Predicted from the curve equation
51N | Neutral time OC | Overcurrent | characteristic | 5 | Timing at 5× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.2500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.195 s | Predicted from the curve equation
50_2 | Negative-sequence IOC | Overcurrent | pickup+time | 1 | Pickup — above threshold | 105% of setting · operating quantity 2.625 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.8750@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate within 0.05 s
50_2 | Negative-sequence IOC | Overcurrent | pickup+time | 2 | Pickup — below threshold | 95% of setting · operating quantity 2.375 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.1250@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
50_2 | Negative-sequence IOC | Overcurrent | pickup+time | 3 | Timing at 2× pickup | Step from prefault zero straight to the test value | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.050 s | Measured from application of current to trip contact
46 | Negative-sequence TOC | Overcurrent | characteristic | 1 | Pickup — above threshold | 105% of setting · operating quantity 1.050 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 3.1500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Long operate time — allow the curve to run out
46 | Negative-sequence TOC | Overcurrent | characteristic | 2 | Pickup — below threshold | 95% of setting · operating quantity 0.950 A sec | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.8500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
46 | Negative-sequence TOC | Overcurrent | characteristic | 3 | Timing at 2× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 6.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.428 s | Predicted from the curve equation
46 | Negative-sequence TOC | Overcurrent | characteristic | 4 | Timing at 3× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 9.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.547 s | Predicted from the curve equation
46 | Negative-sequence TOC | Overcurrent | characteristic | 5 | Timing at 5× pickup | IEEE Ext Inv · TDM 0.15 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.195 s | Predicted from the curve equation
67 | Directional supervision | Ramping | points | 1 | Forward maximum torque | Current at the characteristic angle — deepest into the operate zone. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-45.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup throughout
67 | Directional supervision | Ramping | points | 2 | Reverse maximum torque | Rotated 180° from MTA — deepest into the restrain zone. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@135.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup throughout
67 | Directional supervision | Ramping | points | 3 | Boundary, leading side (inside) | 5° inside the 90° boundary. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@40.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup throughout
67 | Directional supervision | Ramping | points | 4 | Boundary, leading side (outside) | 5° outside the boundary. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@50.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup throughout
67 | Directional supervision | Ramping | points | 5 | Boundary, lagging side (inside) | 5° inside the 90° boundary. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-130.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | FORWARD | Current held at 2.0× pickup throughout
67 | Directional supervision | Ramping | points | 6 | Boundary, lagging side (outside) | 5° outside the boundary. | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 12.0000@-140.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | REVERSE | Current held at 2.0× pickup throughout
27 | Undervoltage | Voltage | pickup+time | 1 | Pickup — below threshold | 95% of setting | 52.654@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 2.00 s
27 | Undervoltage | Voltage | pickup+time | 2 | Pickup — above threshold | 105% of setting | 58.197@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
27 | Undervoltage | Voltage | pickup+time | 3 | Timing at 0.5× pickup | Step from nominal to the test level | 27.713@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 2.00 s | Definite time
27 | Undervoltage | Voltage | pickup+time | 4 | Below minimum operating voltage | Proves the element blocks rather than operating on a dead bus | 4.000@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | BLOCKED | Element inhibited
59 | Overvoltage | Voltage | pickup+time | 1 | Pickup — above threshold | 105% of setting | 80.021@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Operate after 1.00 s
59 | Overvoltage | Voltage | pickup+time | 2 | Pickup — below threshold | 95% of setting | 72.400@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | No operation
59 | Overvoltage | Voltage | pickup+time | 3 | Timing at 1.3× pickup | Step from nominal to the test level | 99.073@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.00 s | Definite time
59N | Neutral overvoltage | Quick CMC | points | 1 | Pickup — above threshold | 3V0 = 10.50 V secondary | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 10.500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Operate after 1.00 s
59N | Neutral overvoltage | Quick CMC | points | 2 | Pickup — below threshold | 3V0 = 9.50 V secondary | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 9.500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | RESTRAIN | No operation
24 | Volts per hertz | Quick CMC | points | 1 | 60 Hz — above threshold | 1.155 pu V/Hz requires 80.02 V secondary at 60 Hz | 80.021@0.0 | 80.021@-120.0 | 80.021@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | OPERATE | Operate after 5.0 s
24 | Volts per hertz | Quick CMC | points | 2 | 60 Hz — below threshold | 1.045 pu V/Hz requires 72.40 V secondary at 60 Hz | 72.400@0.0 | 72.400@-120.0 | 72.400@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | RESTRAIN | No operation
24 | Volts per hertz | Quick CMC | points | 3 | 57 Hz — above threshold | 1.155 pu V/Hz requires 76.02 V secondary at 57 Hz | 76.020@0.0 | 76.020@-120.0 | 76.020@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 57 | yes | OPERATE | Operate after 5.0 s
24 | Volts per hertz | Quick CMC | points | 4 | 57 Hz — below threshold | 1.045 pu V/Hz requires 68.78 V secondary at 57 Hz | 68.780@0.0 | 68.780@-120.0 | 68.780@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 57 | yes | RESTRAIN | No operation
24 | Volts per hertz | Quick CMC | points | 5 | 54 Hz — above threshold | 1.155 pu V/Hz requires 72.02 V secondary at 54 Hz | 72.019@0.0 | 72.019@-120.0 | 72.019@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 54 | yes | OPERATE | Operate after 5.0 s
24 | Volts per hertz | Quick CMC | points | 6 | 54 Hz — below threshold | 1.045 pu V/Hz requires 65.16 V secondary at 54 Hz | 65.160@0.0 | 65.160@-120.0 | 65.160@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 54 | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 1 | Pickup — past threshold | 0.100 Hz beyond the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.2 | yes | OPERATE | Operate after 0.30 s
81 | Under / over frequency | Quick CMC | points | 2 | Pickup — short of threshold | 0.100 Hz on the healthy side | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.4 | yes | RESTRAIN | No operation
81 | Under / over frequency | Quick CMC | points | 3 | Timing | Step from 60.0 Hz straight to 59.200 Hz | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.2 | yes | 0.300 s | Definite time
81 | Under / over frequency | Quick CMC | points | 4 | Below minimum voltage | Frequency past the setting but voltage held under the 30 V supervision level | 24.000@0.0 | 24.000@-120.0 | 24.000@120.0 |  | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 59.2 | yes | BLOCKED | Element inhibited
32 | Directional power | Quick CMC | points | 1 | Pickup — above threshold | 110% of setting — 191.3 W secondary, 0.660 MW primary | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.9204@0.0 | 0.9204@-120.0 | 0.9204@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | OPERATE | Balanced 3-phase, current at +0.0°
32 | Directional power | Quick CMC | points | 2 | Pickup — below threshold | 90% of setting — 156.5 W secondary, 0.540 MW primary | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.7531@0.0 | 0.7531@-120.0 | 0.7531@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | RESTRAIN | Balanced 3-phase, current at +0.0°
32 | Directional power | Quick CMC | points | 3 | Timing at 2× pickup | 200% of setting — 347.8 W secondary, 1.200 MW primary | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.6735@0.0 | 1.6735@-120.0 | 1.6735@120.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 1.00 s | Balanced 3-phase, current at +0.0°
49 | Thermal overload | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | Applied 7.875 A sec · prior load 0.00× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 7.8750@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 176.3 s | 2.94 minutes
49 | Thermal overload | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | Applied 10.500 A sec · prior load 0.00× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 10.5000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 86.3 s | 1.44 minutes
49 | Thermal overload | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | Applied 15.750 A sec · prior load 0.00× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 15.7500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 35.3 s | 0.59 minutes
49 | Thermal overload | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | Applied 26.250 A sec · prior load 0.00× Ib | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 26.2500@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 12.2 s | 0.20 minutes
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | 105% of detector setting, no initiate | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 1.0500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | DETECTOR PICKED UP | Flag only — no trip without initiate
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | 95% of detector setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.9500@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | NO PICKUP | Detector must drop out
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | Initiate asserted with current held at 2× detector and never removed | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.100 s | Timer 1 — retrip output
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | Same state, second stage | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 2.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | 0.200 s | Timer 2 — bus / backup trip output
50BF | Breaker failure | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | Initiate asserted, then current removed inside timer 1 | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 |  | 0.0000@-75.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 60 | yes | NO TRIP | Proves the detector reset stops the scheme
25 | Synchrocheck | Synchronizer | points | 1 | In synchronism | All three differences comfortably inside their limits | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@16.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz
25 | Synchrocheck | Synchronizer | points | 2 | Angle just inside limit | Angle difference at 80% of the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@16.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | CLOSE PERMITTED | Δθ 16.0°
25 | Synchrocheck | Synchronizer | points | 3 | Angle just outside limit | Angle difference at 120% of the setting | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@24.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | BLOCKED | Δθ 24.0°
25 | Synchrocheck | Synchronizer | points | 4 | Voltage difference outside limit | Angle matched, magnitude offset past ΔV | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 57.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | BLOCKED | ΔV 12.00 V
25 | Synchrocheck | Synchronizer | points | 5 | Slip outside limit | Line output run off frequency so the angle rotates | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 69.282@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | BLOCKED | Δf 0.120 Hz
25 | Synchrocheck | Synchronizer | points | 6 | Dead line, live bus | Line collapsed below the dead threshold | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled
25 | Synchrocheck | Synchronizer | points | 7 | Both dead | Bus and line both below the dead threshold — set the bus channels low as well | 69.282@0.0 | 69.282@-120.0 | 69.282@120.0 | 10.000@0.0 | 0.0000@0.0 | 0.0000@0.0 | 0.0000@0.0 |  |  |  | 60 | yes | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step

## Channels
Function | Description | Group | TU module | Drive as | # | Test step | Channel | Magnitude | Unit | Angle deg | Hz | Note | Expected | Expected — detail | Verdict
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I A-L1 | 1.6735 | A | 0 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I A-L2 | 1.6735 | A | -120 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I A-L3 | 1.6735 | A | 120 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I B-L1 | 0.9762 | A | 150 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I B-L2 | 0.9762 | A | 30 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 1 | Irest 0.5 pu — above slope | I B-L3 | 0.9762 | A | -90 | 60 |  | OPERATE | IW1 0.500 pu · IW2 0.280 pu | op
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I A-L1 | 1.6735 | A | 0 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I A-L2 | 1.6735 | A | -120 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I A-L3 | 1.6735 | A | 120 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I B-L1 | 1.1157 | A | 150 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I B-L2 | 1.1157 | A | 30 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 2 | Irest 0.5 pu — below slope | I B-L3 | 1.1157 | A | -90 | 60 |  | RESTRAIN | IW1 0.500 pu · IW2 0.320 pu | no
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | I A-L1 | 5.0204 | A | 0 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | I A-L2 | 5.0204 | A | -120 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | I A-L3 | 5.0204 | A | 120 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | I B-L1 | 3.7915 | A | 150 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | I B-L2 | 3.7915 | A | 30 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 3 | Irest 1.5 pu — above slope | I B-L3 | 3.7915 | A | -90 | 60 |  | OPERATE | IW1 1.500 pu · IW2 1.087 pu | op
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | I A-L1 | 5.0204 | A | 0 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | I A-L2 | 5.0204 | A | -120 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | I A-L3 | 5.0204 | A | 120 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | I B-L1 | 4.053 | A | 150 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | I B-L2 | 4.053 | A | 30 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 4 | Irest 1.5 pu — below slope | I B-L3 | 4.053 | A | -90 | 60 |  | RESTRAIN | IW1 1.500 pu · IW2 1.163 pu | no
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | I A-L1 | 10.0409 | A | 0 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | I A-L2 | 10.0409 | A | -120 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | I A-L3 | 10.0409 | A | 120 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | I B-L1 | 7.583 | A | 150 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | I B-L2 | 7.583 | A | 30 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 5 | Irest 3 pu — above slope | I B-L3 | 7.583 | A | -90 | 60 |  | OPERATE | IW1 3.000 pu · IW2 2.175 pu | op
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | I A-L1 | 10.0409 | A | 0 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | I A-L2 | 10.0409 | A | -120 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | I A-L3 | 10.0409 | A | 120 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | I B-L1 | 8.1059 | A | 150 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | I B-L2 | 8.1059 | A | 30 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 6 | Irest 3 pu — below slope | I B-L3 | 8.1059 | A | -90 | 60 |  | RESTRAIN | IW1 3.000 pu · IW2 2.325 pu | no
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | I A-L1 | 23.4287 | A | 0 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | I A-L2 | 23.4287 | A | -120 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | I A-L3 | 23.4287 | A | 120 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | I B-L1 | 16.3513 | A | 150 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | I B-L2 | 16.3513 | A | 30 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 7 | Irest 7 pu — above slope | I B-L3 | 16.3513 | A | -90 | 60 |  | OPERATE | IW1 7.000 pu · IW2 4.690 pu | op
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | I A-L1 | 23.4287 | A | 0 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | I A-L2 | 23.4287 | A | -120 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | I A-L3 | 23.4287 | A | 120 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | I B-L1 | 17.8156 | A | 150 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | I B-L2 | 17.8156 | A | 30 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T | Percent differential | Differential | Differential | characteristic | 8 | Irest 7 pu — below slope | I B-L3 | 17.8156 | A | -90 | 60 |  | RESTRAIN | IW1 7.000 pu · IW2 5.110 pu | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 1 | 2nd — inrush — above threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 1 | 2nd — inrush — above threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 1 | 2nd — inrush — above threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 1 | 2nd — inrush — above threshold | I A-L1 | 3.347 | A | 0 | 60 | fundamental | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 1 | 2nd — inrush — above threshold | I A-L1 | 0.7363 | A | 0 | 120 | 2nd harmonic — superimposed on the same output | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 2 | 2nd — inrush — below threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 2 | 2nd — inrush — below threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 2 | 2nd — inrush — below threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 2 | 2nd — inrush — below threshold | I A-L1 | 3.347 | A | 0 | 60 | fundamental | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 2 | 2nd — inrush — below threshold | I A-L1 | 0.6025 | A | 0 | 120 | 2nd harmonic — superimposed on the same output | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 3 | 5th — overexcitation — above threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 3 | 5th — overexcitation — above threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 3 | 5th — overexcitation — above threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 3 | 5th — overexcitation — above threshold | I A-L1 | 3.347 | A | 0 | 60 | fundamental | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 3 | 5th — overexcitation — above threshold | I A-L1 | 1.1045 | A | 0 | 300 | 5th harmonic — superimposed on the same output | RESTRAIN | Differential 1.00 pu present throughout | no
87T-H | Harmonic inhibit | Differential | Harmonics | points | 4 | 5th — overexcitation — below threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 4 | 5th — overexcitation — below threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 4 | 5th — overexcitation — below threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 4 | 5th — overexcitation — below threshold | I A-L1 | 3.347 | A | 0 | 60 | fundamental | OPERATE | Differential 1.00 pu present throughout | op
87T-H | Harmonic inhibit | Differential | Harmonics | points | 4 | 5th — overexcitation — below threshold | I A-L1 | 0.9037 | A | 0 | 300 | 5th harmonic — superimposed on the same output | OPERATE | Differential 1.00 pu present throughout | op
87G | Restricted ground fault | Differential | Differential | characteristic | 1 | Sensitivity — above pickup | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate time 0.00 s | op
87G | Restricted ground fault | Differential | Differential | characteristic | 1 | Sensitivity — above pickup | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate time 0.00 s | op
87G | Restricted ground fault | Differential | Differential | characteristic | 1 | Sensitivity — above pickup | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate time 0.00 s | op
87G | Restricted ground fault | Differential | Differential | characteristic | 1 | Sensitivity — above pickup | I A-L1 | 0.55 | A | 0 | 60 | ground / neutral CT input | OPERATE | Operate time 0.00 s | op
87G | Restricted ground fault | Differential | Differential | characteristic | 2 | Sensitivity — below pickup | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Operate time 0.00 s | no
87G | Restricted ground fault | Differential | Differential | characteristic | 2 | Sensitivity — below pickup | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Operate time 0.00 s | no
87G | Restricted ground fault | Differential | Differential | characteristic | 2 | Sensitivity — below pickup | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Operate time 0.00 s | no
87G | Restricted ground fault | Differential | Differential | characteristic | 2 | Sensitivity — below pickup | I A-L1 | 0.45 | A | 0 | 60 | ground / neutral CT input | RESTRAIN | Operate time 0.00 s | no
87G | Restricted ground fault | Differential | Differential | characteristic | 3 | Through-fault stability | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation at any point of the ramp | no
87G | Restricted ground fault | Differential | Differential | characteristic | 3 | Through-fault stability | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation at any point of the ramp | no
87G | Restricted ground fault | Differential | Differential | characteristic | 3 | Through-fault stability | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation at any point of the ramp | no
87G | Restricted ground fault | Differential | Differential | characteristic | 3 | Through-fault stability | I A-L1 | 20 | A | 0 | 60 | W2 phase L1 | RESTRAIN | No operation at any point of the ramp | no
87G | Restricted ground fault | Differential | Differential | characteristic | 3 | Through-fault stability | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation at any point of the ramp | no
87G | Restricted ground fault | Differential | Differential | characteristic | 3 | Through-fault stability | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation at any point of the ramp | no
87G | Restricted ground fault | Differential | Differential | characteristic | 3 | Through-fault stability | I B-L1 | 120 | A | 180 | 60 | ground / neutral CT input, reversed polarity | RESTRAIN | No operation at any point of the ramp | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L1 | 42 | A | -75 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L1 | 38 | A | -75 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L1 | 80 | A | -75 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50P | Phase instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 6.3 | A | -75 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 5.7 | A | -75 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L1 | 12 | A | -75 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L1 | 18 | A | -75 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L1 | 30 | A | -75 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51P | Phase time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L1 | 2.625 | A | -75 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L1 | 2.375 | A | -75 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L1 | 5 | A | -75 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50G | Ground instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 1.05 | A | -75 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 0.95 | A | -75 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L1 | 2 | A | -75 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L1 | 3 | A | -75 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L1 | 5 | A | -75 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51G | Ground time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L1 | 3.15 | A | -75 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L1 | 2.85 | A | -75 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L1 | 6 | A | -75 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50N | Neutral instantaneous OC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 1.3125 | A | -75 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 1.1875 | A | -75 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L1 | 2.5 | A | -75 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L1 | 3.75 | A | -75 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L1 | 6.25 | A | -75 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
51N | Neutral time OC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L1 | 7.875 | A | -75 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate within 0.05 s | op
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L1 | 7.125 | A | -75 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L1 | 15 | A | -75 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
50_2 | Negative-sequence IOC | Overcurrent | Overcurrent | pickup+time | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.050 s | Measured from application of current to trip contact | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L1 | 3.15 | A | -75 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Long operate time — allow the curve to run out | op
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L1 | 2.85 | A | -75 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L1 | 6 | A | -75 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.428 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L1 | 9 | A | -75 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 4 | Timing at 3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.547 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L1 | 69.282 | V | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L1 | 15 | A | -75 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
46 | Negative-sequence TOC | Overcurrent | Overcurrent | characteristic | 5 | Timing at 5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 0.195 s | Predicted from the curve equation | nu
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | I A-L1 | 12 | A | -45 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | I A-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | I A-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | I B-L1 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | I B-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 1 | Forward maximum torque | I B-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | I A-L1 | 12 | A | 135 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | I A-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | I A-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | I B-L1 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | I B-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 2 | Reverse maximum torque | I B-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | I A-L1 | 12 | A | 40 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | I A-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | I A-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | I B-L1 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | I B-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 3 | Boundary, leading side (inside) | I B-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | I A-L1 | 12 | A | 50 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | I A-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | I A-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | I B-L1 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | I B-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 4 | Boundary, leading side (outside) | I B-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | V L1 | 69.282 | V | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | V L2 | 69.282 | V | -120 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | V L3 | 69.282 | V | 120 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | I A-L1 | 12 | A | -130 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | I A-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | I A-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | I B-L1 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | I B-L2 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 5 | Boundary, lagging side (inside) | I B-L3 | 0 | A | 0 | 60 |  | FORWARD | Current held at 2.0× pickup throughout | op
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | V L1 | 69.282 | V | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | V L2 | 69.282 | V | -120 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | V L3 | 69.282 | V | 120 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | I A-L1 | 12 | A | -140 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | I A-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | I A-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | I B-L1 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | I B-L2 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
67 | Directional supervision | Directional | Ramping | points | 6 | Boundary, lagging side (outside) | I B-L3 | 0 | A | 0 | 60 |  | REVERSE | Current held at 2.0× pickup throughout | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | V L1 | 52.654 | V | 0 | 60 | depressed phase | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 2.00 s | op
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | V L1 | 58.197 | V | 0 | 60 | depressed phase | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | V L1 | 27.713 | V | 0 | 60 | depressed phase | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | V L2 | 69.282 | V | -120 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | V L3 | 69.282 | V | 120 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | I A-L1 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | I A-L2 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | I A-L3 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | I B-L1 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | I B-L2 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 0.5× pickup | I B-L3 | 0 | A | 0 | 60 |  | 2.00 s | Definite time | nu
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | V L1 | 4 | V | 0 | 60 | depressed phase | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I B-L1 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I B-L2 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
27 | Undervoltage | Voltage & frequency | Voltage | pickup+time | 4 | Below minimum operating voltage | I B-L3 | 0 | A | 0 | 60 |  | BLOCKED | Element inhibited | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | V L1 | 80.021 | V | 0 | 60 | raised phase | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | V L1 | 72.4 | V | 0 | 60 | raised phase | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | V L1 | 99.073 | V | 0 | 60 | raised phase | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | I A-L1 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | I A-L2 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | I A-L3 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59 | Overvoltage | Voltage & frequency | Voltage | pickup+time | 3 | Timing at 1.3× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.00 s | Definite time | nu
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Operate after 1.00 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Operate after 1.00 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | V 4 | 10.5 | V | 0 | 60 | broken-delta 3V0 input | OPERATE | Operate after 1.00 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 1 | Pickup — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 1.00 s | op
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | V 4 | 9.5 | V | 0 | 60 | broken-delta 3V0 input | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
59N | Neutral overvoltage | Voltage & frequency | Quick CMC | points | 2 | Pickup — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 1 | 60 Hz — above threshold | V L1 | 80.021 | V | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 1 | 60 Hz — above threshold | V L2 | 80.021 | V | -120 | 60 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 1 | 60 Hz — above threshold | V L3 | 80.021 | V | 120 | 60 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 1 | 60 Hz — above threshold | I A-L1 | 0 | A | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 1 | 60 Hz — above threshold | I A-L2 | 0 | A | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 1 | 60 Hz — above threshold | I A-L3 | 0 | A | 0 | 60 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 2 | 60 Hz — below threshold | V L1 | 72.4 | V | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 2 | 60 Hz — below threshold | V L2 | 72.4 | V | -120 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 2 | 60 Hz — below threshold | V L3 | 72.4 | V | 120 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 2 | 60 Hz — below threshold | I A-L1 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 2 | 60 Hz — below threshold | I A-L2 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 2 | 60 Hz — below threshold | I A-L3 | 0 | A | 0 | 60 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 3 | 57 Hz — above threshold | V L1 | 76.02 | V | 0 | 57 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 3 | 57 Hz — above threshold | V L2 | 76.02 | V | -120 | 57 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 3 | 57 Hz — above threshold | V L3 | 76.02 | V | 120 | 57 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 3 | 57 Hz — above threshold | I A-L1 | 0 | A | 0 | 57 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 3 | 57 Hz — above threshold | I A-L2 | 0 | A | 0 | 57 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 3 | 57 Hz — above threshold | I A-L3 | 0 | A | 0 | 57 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 4 | 57 Hz — below threshold | V L1 | 68.78 | V | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 4 | 57 Hz — below threshold | V L2 | 68.78 | V | -120 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 4 | 57 Hz — below threshold | V L3 | 68.78 | V | 120 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 4 | 57 Hz — below threshold | I A-L1 | 0 | A | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 4 | 57 Hz — below threshold | I A-L2 | 0 | A | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 4 | 57 Hz — below threshold | I A-L3 | 0 | A | 0 | 57 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 5 | 54 Hz — above threshold | V L1 | 72.019 | V | 0 | 54 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 5 | 54 Hz — above threshold | V L2 | 72.019 | V | -120 | 54 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 5 | 54 Hz — above threshold | V L3 | 72.019 | V | 120 | 54 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 5 | 54 Hz — above threshold | I A-L1 | 0 | A | 0 | 54 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 5 | 54 Hz — above threshold | I A-L2 | 0 | A | 0 | 54 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 5 | 54 Hz — above threshold | I A-L3 | 0 | A | 0 | 54 |  | OPERATE | Operate after 5.0 s | op
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 6 | 54 Hz — below threshold | V L1 | 65.16 | V | 0 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 6 | 54 Hz — below threshold | V L2 | 65.16 | V | -120 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 6 | 54 Hz — below threshold | V L3 | 65.16 | V | 120 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 6 | 54 Hz — below threshold | I A-L1 | 0 | A | 0 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 6 | 54 Hz — below threshold | I A-L2 | 0 | A | 0 | 54 |  | RESTRAIN | No operation | no
24 | Volts per hertz | Voltage & frequency | Quick CMC | points | 6 | 54 Hz — below threshold | I A-L3 | 0 | A | 0 | 54 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | V L1 | 69.282 | V | 0 | 59.2 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | V L2 | 69.282 | V | -120 | 59.2 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | V L3 | 69.282 | V | 120 | 59.2 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | I A-L1 | 0 | A | 0 | 59.2 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | I A-L2 | 0 | A | 0 | 59.2 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 1 | Pickup — past threshold | I A-L3 | 0 | A | 0 | 59.2 |  | OPERATE | Operate after 0.30 s | op
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | V L1 | 69.282 | V | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | V L2 | 69.282 | V | -120 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | V L3 | 69.282 | V | 120 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | I A-L1 | 0 | A | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | I A-L2 | 0 | A | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 2 | Pickup — short of threshold | I A-L3 | 0 | A | 0 | 59.4 |  | RESTRAIN | No operation | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | V L1 | 69.282 | V | 0 | 59.2 | step from 60.0 Hz | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | V L2 | 69.282 | V | -120 | 59.2 | step from 60.0 Hz | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | V L3 | 69.282 | V | 120 | 59.2 | step from 60.0 Hz | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | I A-L1 | 0 | A | 0 | 59.2 | step from 60.0 Hz | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | I A-L2 | 0 | A | 0 | 59.2 | step from 60.0 Hz | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 3 | Timing | I A-L3 | 0 | A | 0 | 59.2 | step from 60.0 Hz | 0.300 s | Definite time | nu
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | V L1 | 24 | V | 0 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | V L2 | 24 | V | -120 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | V L3 | 24 | V | 120 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | I A-L1 | 0 | A | 0 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | I A-L2 | 0 | A | 0 | 59.2 |  | BLOCKED | Element inhibited | no
81 | Under / over frequency | Voltage & frequency | Quick CMC | points | 4 | Below minimum voltage | I A-L3 | 0 | A | 0 | 59.2 |  | BLOCKED | Element inhibited | no
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | V L1 | 69.282 | V | 0 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | V L2 | 69.282 | V | -120 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | V L3 | 69.282 | V | 120 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | I A-L1 | 0.9204 | A | 0 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | I A-L2 | 0.9204 | A | -120 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | I A-L3 | 0.9204 | A | 120 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | I B-L1 | 0 | A | 0 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | I B-L2 | 0 | A | 0 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 1 | Pickup — above threshold | I B-L3 | 0 | A | 0 | 60 |  | OPERATE | Balanced 3-phase, current at +0.0° | op
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | V L1 | 69.282 | V | 0 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | V L2 | 69.282 | V | -120 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | V L3 | 69.282 | V | 120 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | I A-L1 | 0.7531 | A | 0 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | I A-L2 | 0.7531 | A | -120 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | I A-L3 | 0.7531 | A | 120 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | I B-L1 | 0 | A | 0 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | I B-L2 | 0 | A | 0 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 2 | Pickup — below threshold | I B-L3 | 0 | A | 0 | 60 |  | RESTRAIN | Balanced 3-phase, current at +0.0° | no
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | V L1 | 69.282 | V | 0 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | V L2 | 69.282 | V | -120 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | V L3 | 69.282 | V | 120 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | I A-L1 | 1.6735 | A | 0 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | I A-L2 | 1.6735 | A | -120 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | I A-L3 | 1.6735 | A | 120 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | I B-L1 | 0 | A | 0 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | I B-L2 | 0 | A | 0 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
32 | Directional power | Directional | Quick CMC | points | 3 | Timing at 2× pickup | I B-L3 | 0 | A | 0 | 60 |  | 1.00 s | Balanced 3-phase, current at +0.0° | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | I A-L1 | 7.875 | A | 0 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 1 | Operate at 1.5× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 176.3 s | 2.94 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | I A-L1 | 10.5 | A | 0 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 2 | Operate at 2× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 86.3 s | 1.44 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | I A-L1 | 15.75 | A | 0 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 3 | Operate at 3× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 35.3 s | 0.59 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | V L1 | 69.282 | V | 0 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | V L2 | 69.282 | V | -120 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | V L3 | 69.282 | V | 120 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | I A-L1 | 26.25 | A | 0 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | I A-L2 | 0 | A | 0 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | I A-L3 | 0 | A | 0 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | I B-L1 | 0 | A | 0 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | I B-L2 | 0 | A | 0 | 60 |  | 12.2 s | 0.20 minutes | nu
49 | Thermal overload | Overcurrent | Overcurrent | characteristic | 4 | Operate at 5× thermal setting | I B-L3 | 0 | A | 0 | 60 |  | 12.2 s | 0.20 minutes | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | V L1 | 69.282 | V | 0 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | V L2 | 69.282 | V | -120 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | V L3 | 69.282 | V | 120 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | I A-L1 | 1.05 | A | -75 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | I A-L2 | 0 | A | 0 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | I A-L3 | 0 | A | 0 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | I B-L1 | 0 | A | 0 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | I B-L2 | 0 | A | 0 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 1 | Current detector — above threshold | I B-L3 | 0 | A | 0 | 60 |  | DETECTOR PICKED UP | Flag only — no trip without initiate | op
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | V L1 | 69.282 | V | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | V L2 | 69.282 | V | -120 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | V L3 | 69.282 | V | 120 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | I A-L1 | 0.95 | A | -75 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | I A-L2 | 0 | A | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | I A-L3 | 0 | A | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | I B-L1 | 0 | A | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | I B-L2 | 0 | A | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 2 | Current detector — below threshold | I B-L3 | 0 | A | 0 | 60 |  | NO PICKUP | Detector must drop out | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | V L1 | 69.282 | V | 0 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | V L2 | 69.282 | V | -120 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | V L3 | 69.282 | V | 120 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | I A-L1 | 2 | A | -75 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | I A-L2 | 0 | A | 0 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | I A-L3 | 0 | A | 0 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | I B-L1 | 0 | A | 0 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | I B-L2 | 0 | A | 0 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 3 | Retrip timing | I B-L3 | 0 | A | 0 | 60 |  | 0.100 s | Timer 1 — retrip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | V L1 | 69.282 | V | 0 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | V L2 | 69.282 | V | -120 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | V L3 | 69.282 | V | 120 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | I A-L1 | 2 | A | -75 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | I A-L2 | 0 | A | 0 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | I A-L3 | 0 | A | 0 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | I B-L1 | 0 | A | 0 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | I B-L2 | 0 | A | 0 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 4 | Backup trip timing | I B-L3 | 0 | A | 0 | 60 |  | 0.200 s | Timer 2 — bus / backup trip output | nu
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | V L1 | 69.282 | V | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | V L2 | 69.282 | V | -120 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | V L3 | 69.282 | V | 120 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | I A-L1 | 0 | A | -75 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | I A-L2 | 0 | A | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | I A-L3 | 0 | A | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | I B-L1 | 0 | A | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | I B-L2 | 0 | A | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
50BF | Breaker failure | Overcurrent | State Sequencer | sequence (assemble from these steps) | 5 | Reset check | I B-L3 | 0 | A | 0 | 60 |  | NO TRIP | Proves the detector reset stops the scheme | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V L1 | 69.282 | V | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V L2 | 69.282 | V | -120 | 60 |  | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V L3 | 69.282 | V | 120 | 60 |  | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | V 4 | 69.282 | V | 16 | 60 | line side | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | I A-L1 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | I A-L2 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 1 | In synchronism | I A-L3 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0°, ΔV 0 V, Δf 0 Hz | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V L1 | 69.282 | V | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V L2 | 69.282 | V | -120 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V L3 | 69.282 | V | 120 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | V 4 | 69.282 | V | 16 | 60 | line side | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | I A-L1 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | I A-L2 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 2 | Angle just inside limit | I A-L3 | 0 | A | 0 | 60 |  | CLOSE PERMITTED | Δθ 16.0° | op
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | V 4 | 69.282 | V | 24 | 60 | line side | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 3 | Angle just outside limit | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | Δθ 24.0° | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | V 4 | 57.282 | V | 0 | 60 | line side | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 4 | Voltage difference outside limit | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | ΔV 12.00 V | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V L1 | 69.282 | V | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V L2 | 69.282 | V | -120 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V L3 | 69.282 | V | 120 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | V 4 | 69.282 | V | 0 | 60.12 | line side — 60.120 Hz | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | I A-L1 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | I A-L2 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 5 | Slip outside limit | I A-L3 | 0 | A | 0 | 60 |  | BLOCKED | Δf 0.120 Hz | no
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus | V L1 | 69.282 | V | 0 | 60 |  | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus | V L2 | 69.282 | V | -120 | 60 |  | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus | V L3 | 69.282 | V | 120 | 60 |  | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus | V 4 | 10 | V | 0 | 60 | line side | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus | I A-L1 | 0 | A | 0 | 60 |  | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus | I A-L2 | 0 | A | 0 | 60 |  | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 6 | Dead line, live bus | I A-L3 | 0 | A | 0 | 60 |  | PER DEAD-LINE LOGIC | Result depends on the dead/live scheme enabled | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead | V L1 | 69.282 | V | 0 | 60 |  | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead | V L2 | 69.282 | V | -120 | 60 |  | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead | V L3 | 69.282 | V | 120 | 60 |  | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead | V 4 | 10 | V | 0 | 60 | line side | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead | I A-L1 | 0 | A | 0 | 60 |  | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead | I A-L2 | 0 | A | 0 | 60 |  | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step | nu
25 | Synchrocheck | Voltage & frequency | Synchronizer | points | 7 | Both dead | I A-L3 | 0 | A | 0 | 60 |  | PER DEAD-BUS LOGIC | Drop the three bus channels to 10.0 V for this step | nu

## Build guide
Building the 845 OCC in Test Universe
Assembles `845-VEC-steps.csv` and `845-VEC-channels.csv` into one Test Universe document —
21 elements, 91 steps. Build it once and save it as a template; the next transformer is a
re-point of the test object.
Values below are for the tool's **sample** transformer: 20 MVA, 115 / 13.8 kV, **Dyn1**,
60 Hz, W1 CT 150:5 wye, W2 CT 1200:5 wye, ground CT 200:5, VT 13800:120 wye on W2, REF on
W2. Enter your real transformer in `845.html` and re-run the generator.
---
1 · The vector group is the test
Everything difficult about a transformer differential comes from the fact that the two
windings do not see the same thing, and almost every false result comes from getting that
wrong on the test set rather than in the relay.
The sample is **Dyn1**: W2 lags W1 by 30°. The plan handles it by injecting the W2 triple
at **150°**, so a through condition lands on the relay's own internal compensation and
nets to zero differential. If you build the W2 triple at 180° — the intuitive
"opposed" answer that is correct for a generator or a line — every through-current step
will show a standing differential of about 0.518 pu and look exactly like a wiring fault.
Check three things before anything else:
1. **The vector group in the relay** matches the nameplate and matches what the tool is
set to. `Dyn1` and `Dyn11` differ by 60° and both are common.
2. **Which winding the relay compensates.** The plan assumes the relay does the
compensation internally and the CTs are wye on both sides. If the CTs are delta on one
side the compensation is already in the wiring and applying it again doubles it.
3. **Per unit is per winding.** One per unit is 3.347 A secondary on W1 and 3.486 A on W2.
They are deliberately different numbers, because the CT ratios do not match the turns
ratio exactly — which is the normal case. A test built on one number for both windings
is wrong on one of them.
2 · Test object
¦ Field ¦ Sample value ¦ Where it comes from ¦
¦-------¦--------------¦---------------------¦
¦ Nominal voltage, secondary ¦ 120 V L–L (69.282 V L–N) ¦ VT 13800 : 120, on W2 ¦
¦ Nominal current, secondary ¦ 5 A ¦ CT secondary, both windings ¦
¦ VT ratio ¦ 115 : 1 ¦ ¦
¦ CT ratio, W1 ¦ 30 : 1 ¦ 150 : 5 ¦
¦ CT ratio, W2 ¦ 240 : 1 ¦ 1200 : 5 ¦
¦ CT ratio, ground ¦ 40 : 1 ¦ 200 : 5 ¦
¦ Nominal frequency ¦ 60 Hz ¦ ¦
¦ Vector group ¦ Dyn1 — W2 30° behind W1 ¦ nameplate ¦
Rated currents, which every per-unit value in the plan is referred to:
¦ Winding ¦ Primary ¦ Secondary ¦
¦---¦---:¦---:¦
¦ W1 (115 kV) ¦ 100.4 A ¦ **3.347 A** ¦
¦ W2 (13.8 kV) ¦ 836.7 A ¦ **3.486 A** ¦
The VT is on **W2**. Every voltage-dependent element in the plan — 27, 59, 24, 32, 59N,
25 — measures the W2 side, and the tool follows the winding you select rather than
assuming W1. If your VT is on the other side, change it in the tool, not in your head.
3 · Hardware configuration
**Amplifier mode: 6 × 12.5 A, two triples.** `I A-*` is W1, `I B-*` is W2. The
differential and REF both need two triples; nothing else does. See §7 — the 12.5 A cap
this buys you is the plan's main constraint.
**V 4 does two different jobs** and cannot do both at once:
¦ Used by ¦ V 4 carries ¦
¦---¦---¦
¦ 59N ¦ Broken-delta 3V0 input ¦
¦ 25 ¦ Line side, at 60.120 Hz for the slip case ¦
That is a re-patch at the terminal block between two groups of steps, not a software
change. Section 4 orders the modules so it happens once.
Declare V 4 as an independent generator rather than a copy of V L1 — the synchrocheck slip
case needs it running at its own frequency.
Binary I/O
¦ CMC ¦ Direction ¦ To / from the relay ¦
¦-----¦-----------¦---------------------¦
¦ Bin. in 1 ¦ in ¦ Trip / 86 lockout — the timing reference for every operate time ¦
¦ Bin. in 2 ¦ in ¦ Close permissive — 25 ¦
¦ Bin. in 3 ¦ in ¦ Alarm, on the elements that alarm before they trip ¦
¦ Bin. out 1 ¦ out ¦ 52a ¦
¦ Bin. out 2 ¦ out ¦ 52b ¦
¦ Bin. out 3 ¦ out ¦ Breaker-failure initiate ¦
4 · Module map
Filter `845-VEC-steps.csv` on `TU_Module`. Ordered so the V 4 patch changes once and the
two-triple work is grouped:
¦ Order ¦ Module ¦ Elements ¦ Steps ¦
¦------:¦--------¦----------¦------:¦
¦ 1 ¦ Overcurrent — pickup + time ¦ 50P, 50G, 50N, 50_2 ¦ 12 ¦
¦ 2 ¦ Overcurrent — characteristic ¦ 51P, 51G, 51N, 46, 49 ¦ 24 ¦
¦ 3 ¦ Voltage ¦ 27, 59 ¦ 7 ¦
¦ 4 ¦ Ramping ¦ 67 ¦ 6 ¦
¦ 5 ¦ State Sequencer ¦ 50BF (assembled from 5 steps) ¦ 5 ¦
¦ — ¦ *V 4 to broken delta* ¦ ¦ ¦
¦ 6 ¦ Quick CMC ¦ 59N, 24, 81, 32 ¦ 15 ¦
¦ — ¦ *V 4 to line side* ¦ ¦ ¦
¦ 7 ¦ Synchronizer ¦ 25 ¦ 7 ¦
¦ 8 ¦ Differential ¦ 87T, 87G ¦ 11 ¦
¦ 9 ¦ Harmonics ¦ 87T-H ¦ 4 ¦
5 · The Differential module — 87T and 87G
**87T percent differential**, eight points across four restraint values, with the
characteristic entered once: pickup 0.20 pu, slope 1 25 % to a breakpoint of 2.0 pu, slope
2 60 % beyond 6.0 pu, restraint taken as max(¦IW1¦,¦IW2¦).
Confirm the **restraint definition** in the relay before trusting a slope point. Sum,
maximum and average put the device at different places on the characteristic for the same
pair of currents, and a mismatch produces points that are all plausible and all wrong.
Two things the plan does that are easy to undo by hand:
- **W2 is injected at 150°, not 180°.** That is the Dyn1 compensation. See §1.
- **The two windings carry different magnitudes for the same per unit** — 3.347 A against
3.486 A. That is not a rounding error, it is the CT ratio mismatch, and it is what the
relay's own per-winding scaling is there to remove.
The through-current step is worth more than every threshold in the module. It proves the
vector-group compensation, both CT ratios and both polarities at once, and it is the one
that fails when something is genuinely wrong.
**87G restricted earth fault**, on W2. Pickup 0.500 A secondary, 20.0 A primary. The phase
CTs are 1200:5 and the ground CT is 200:5, so the stability injection is scaled for that
difference — both inputs see the same primary amperes. Do not "correct" the two channels
back to the same secondary value.
REF is a polarity test as much as a level test. If the stability point operates, the
ground CT or one phase CT is reversed. Chase the wiring; do not touch the slope.
6 · Harmonic inhibit — the only test that proves inrush restraint
`87T-H` puts the fundamental and the harmonic on the **same physical output**,
superimposed. Build it in the Harmonics module, or as a superimposed signal in State
Sequencer.
¦ Component ¦ At the setting ¦
¦---¦---:¦
¦ Fundamental ¦ 3.347 A ¦
¦ 2nd harmonic, 20 % ¦ 0.669 A ¦
¦ 5th harmonic, 30 % ¦ 1.004 A ¦
**Energise one winding only.** Leave the other triple at zero so the relay sees full
unrestrained differential and the harmonic content is the only thing deciding the outcome.
A balanced through-injection with harmonics added proves nothing, because there is no
differential to inhibit.
An ordinary differential test contains no harmonics and always releases the element. If
the only inrush evidence on the record is that the differential operated on a clean
injection, inrush restraint has not been tested.
7 · Before you inject — the amplifier conflict
The differential needs two triples, which caps every channel at 12.5 A. One per unit on W1
is 3.347 A, so the highest restraint reachable is 12.5 / 3.347 = **3.73 pu**:
¦ Restraint point ¦ W1 current ¦ 6 × 12.5 A ¦
¦---¦---:¦---¦
¦ 0.50 pu ¦ 1.6735 A ¦ fine ¦
¦ 1.50 pu ¦ 5.0204 A ¦ fine ¦
¦ 3.00 pu ¦ 10.0409 A ¦ fine ¦
¦ 7.00 pu ¦ 23.4287 A ¦ out of reach ¦
Drop the top restraint point to something the amplifier can produce and record the range
the slope was actually proved over, or add a second amplifier. Do not raise the number and
hope.
**Nine single-triple steps also exceed 12.5 A** and need the amplifier changed to
3 × 32 A, or 1 × 64 A for the largest. Two on 51P, two on 49, one each on 46 and 50_2, and
three on 50P:
¦ Step ¦ Current ¦ Reachable in ¦
¦---¦---:¦---¦
¦ 46 and 50_2 timing at their top multiple ¦ 15.000 A ¦ 3 × 32 A ¦
¦ 49 operate at 3 × and 5 × thermal setting ¦ 15.750 / 26.250 A ¦ 3 × 32 A ¦
¦ 51P timing at 3 × and 5 × pickup ¦ 18.000 / 30.000 A ¦ 3 × 32 A ¦
¦ 50P pickup pair ¦ 42.000 / 38.000 A ¦ 1 × 64 A, single phase ¦
¦ **50P timing at 2 × pickup** ¦ **80.000 A** ¦ **not by a CMC 356 in any mode** ¦
The 87G stability step at 20.000 A is over the cap too, and it needs the second triple —
so it moves with 87T, not with the single-triple group. Run it at a reduced through
current and say so; the polarity finding it exists for does not depend on the level.
50P is set at 8 × CT, which is 40.000 A secondary before any test multiple is applied.
Prove the pickup pair in the 1 × 64 A arrangement and time the element at a lower multiple
— 1.5 × pickup is 60.0 A and still reachable there. Record the multiple you used rather
than dropping the timing test.
8 · Two more things the plan already handles
**Negative-sequence rows carry the ×3.** A single-phase injection produces I2 = I/3, so
50_2 and 46 are listed at three times the setting: 50_2 at 7.500 A for a 2.500 A setting,
46 at three times its 1.000 A pickup. **Do not apply the factor again.** If you would
rather inject a balanced set in reverse rotation, I2 = I instead and the ×3 must come back
out — the tool says so per element.
**49 is a thermal replica with memory.** It uses the IEC 60255-8 form
`t = τ · ln[(I² − Ip²) / (I² − (k·Ib)²)]` with τ = 5 min, and the times in the plan assume
the replica starts at the stated prior load. After a point that reached trip it needs
several time constants to return — around 25 minutes here. Confirm the relay uses this
form and not a discrete-step model before relying on the predicted times, and record the
starting state with every result.
9 · After the first build
Save as a template with the test object detached. The vector-group angle, the V 4 re-patch
point, the module order and the amplifier conflict carry across transformers unchanged;
the ratings, ratios and thresholds come out of the generator.
Two things this plan deliberately will not do: it will not inject W2 at 180° because that
is what "opposed" looks like, and it will not let a clean-injection differential trip
stand as evidence that harmonic inhibit works.